## Read Me
Digital Realty - Future State Maintenance (FSM) PoC Master Data Workbook
Purpose
This workbook defines the CMMS/EAM master data required to stand up the Future State Maintenance Proof of Concept described in 'Scope of Works - Future State Maintenance Proof of Concept' (Aug 12, 2026): representative Digital Realty data center sites across EMEA, NAM, and APAC, condition-monitored via vibration, thermal, and ultrasound sensing layered on existing BMS/EPMS/DCIM/CMMS telemetry.
Important assumption
All facility names, IDs, capacities, and asset lists in this workbook are ILLUSTRATIVE placeholders built to demonstrate the master-data model requested for the Digital Realty Future State Maintenance (FSM) Proof of Concept. They are not confirmed Digital Realty site, asset, or vendor records. Per SOW Section 3.1, final PoC sites must be jointly agreed at project initiation, and per SOW Section 3.3 the Vendor must submit an approved Final Asset Scope Matrix before any installation, integration, or monitoring activity begins. Replace the illustrative rows with confirmed data before operational use.
How this aligns to the SOW
• Sheet 'Asset Register (FASM)' implements the exact minimum field set required by SOW Section 3.3: Asset ID, Asset Name, Asset Class, Site and Physical Location, Asset Criticality Rating, Monitoring Method, Existing Data Source(s), Additional Sensors, Failure Codes Being Monitored, Manufacturer, and Asset Status (Included/Excluded).
• Sheet 'Asset Class Master' reflects the exact Target Asset Classes in SOW Section 3.2 (Mechanical, Electrical, Supporting Systems), plus one clearly flagged supplementary class.
• Sheet 'Failure Code Master' reflects the failure modes named in SOW Sections 4.2-4.4 (Vibration, Thermal, Ultrasound).
• Sheet 'Data Source & System Master' covers all 8 SOW Section 4.1 existing data sources (BMS, EPMS, DCIM, OEM monitoring platforms, Battery Monitoring System, CMMS maintenance history, asset registry information, incident history) plus the three new condition-monitoring technologies, each with a 'Sample Data Location' pointer to the exact sheet carrying its illustrative integrated data.
• Sheet 'Governance & Stakeholder Master' reflects the SOW Section 7.1 stakeholder list.
• Sheet 'PM Task Library (Baseline)' represents the EXISTING calendar-based preventive maintenance that SOW Section 2.2 confirms is explicitly OUT OF SCOPE to remove or replace during the PoC.
• Sheet 'KPI Master' reproduces the Technical and Operational KPI targets from SOW Section 8 verbatim.
Global CMMS/EAM best practices applied
• Hierarchical location model (Site > Building > Floor > Data Hall/Room) so assets roll up to a physical and electrical/mechanical redundancy path, consistent with data-center EAM practice (N / N+1 / 2N).
• Criticality tiering tied to redundancy impact rather than generic High/Med/Low labels, per Uptime Institute / ASHRAE TC 9.9 critical-facilities practice.
• Every asset traceable to a manufacturer, monitoring method, data source system, and failure-mode set - the standard ISO 14224 / RCM (SAE JA1011/JA1012) asset taxonomy used in mission-critical EAM.
• PM baseline separated from the new condition-based pilot so existing regulatory/contractual maintenance (NFPA 70B/70E/110, ASHRAE) is visibly preserved, matching SOW Section 2.2 exclusions.
• Master data normalized into reference tables (Sites, Locations, Asset Classes, Manufacturers, Failure Codes, Systems, Criticality, Stakeholders, KPIs) so the transactional workbook can reference IDs rather than repeating text - standard relational CMMS design.
Companion file
See 'DigitalRealty_FSM_PoC_Transactional_Data.xlsx' for sample Work Orders, Alert & Anomaly Register, Condition Monitoring Readings, Maintenance Correlation Log, PM Compliance Log, Weekly Health Reports, Incident History, Risk Register, and the two PoC readiness checklists required as SOW deliverables.
Workbook map
• 1. Site Master - the 6 illustrative PoC sites (2 per region).
• 2. Location Hierarchy Master - Site > Building > Floor > Data Hall/Room structure.
• 3. Asset Class Master - SOW 3.2 target asset classes with default criticality/monitoring/strategy.
• 4. Manufacturer / OEM Master - representative OEMs per asset class.
• 5. Failure Code Master - SOW 4.2-4.4 vibration/thermal/ultrasound failure modes.
• 6. Asset Register (FASM) - SOW 3.3 deliverable, 48 illustrative assets.
• 7. Criticality Rating Matrix - rating definitions tied to redundancy impact and response SLA.
• 8. Data Source & System Master - BMS/EPMS/DCIM/OEM/CMMS + 3 new sensing platforms.
• 9. Governance & Stakeholder Master - SOW 7.1 stakeholders and RACI.
• 10. PM Task Library (Baseline) - existing calendar-based PM, explicitly preserved per SOW 2.2.
• 11. KPI Master - SOW Section 8 Technical & Operational KPI targets.

## Site Master
Site ID | Site Name | Region | Country | Metro Area | Facility Type | Design Tier | Power Redundancy | Cooling Redundancy | PoC Critical Zone | Total IT Load (MW, illustrative) | Gross Area (sq ft, illustrative) | PoC Status
IAD35 | Ashburn Campus - Building 35 | NAM | United States | Ashburn, Virginia | Hyperscale / Wholesale | Uptime Tier III-equivalent | 2N | N+1 | Data Hall 3, Suite C | 18 | 210000 | Proposed
ORD12 | Franklin Park Campus - Building 12 | NAM | United States | Chicago, Illinois | Colocation / Interconnection | Uptime Tier III-equivalent | N+1 | N+1 | Data Hall 1, Suite A | 9.5 | 140000 | Proposed
LHR10 | London Campus - Building 10 | EMEA | United Kingdom | London (Docklands/Woking) | Colocation / Interconnection | Uptime Tier III-equivalent | 2N | N+1 | Data Hall 2, Suite B | 12 | 165000 | Proposed
FRA15 | Hanauer Landstrasse Campus - Building 15 | EMEA | Germany | Frankfurt | Hyperscale / Interconnection | Uptime Tier III-equivalent | 2N | N+1 | Data Hall 4, Suite D | 20 | 225000 | Proposed
SIN11 | Loyang Campus - Building 11 | APAC | Singapore | Singapore | Colocation / Hyperscale | Uptime Tier III-equivalent | N+1 | N+1 | Data Hall 1, Suite A | 15 | 180000 | Proposed
SYD12 | Erskine Park Campus - Building 12 | APAC | Australia | Sydney | Hyperscale / Wholesale | Uptime Tier III-equivalent | 2N | N+1 | Data Hall 2, Suite B | 11 | 150000 | Proposed

## Location Hierarchy Master
Location ID | Parent Location / Site ID | Site ID | Location Type | Location Name
IAD35-BLDG01 | IAD35 | IAD35 | Building | Ashburn Campus - Building 35
IAD35-FLR01 | IAD35-BLDG01 | IAD35 | Floor | Floor 1 - White Space Level
IAD35-DHPOC | IAD35-FLR01 | IAD35 | Data Hall (PoC Zone) | Data Hall 3, Suite C
IAD35-ELEC01 | IAD35-FLR01 | IAD35 | Electrical Room | Electrical Switchgear Room 1 (serving PoC zone)
IAD35-MECH01 | IAD35-BLDG01 | IAD35 | Mechanical Plant / Yard | Central Utility Plant / Mechanical Yard
IAD35-GENYD01 | IAD35-BLDG01 | IAD35 | Generator Yard | Standby Generator Yard
ORD12-BLDG01 | ORD12 | ORD12 | Building | Franklin Park Campus - Building 12
ORD12-FLR01 | ORD12-BLDG01 | ORD12 | Floor | Floor 1 - White Space Level
ORD12-DHPOC | ORD12-FLR01 | ORD12 | Data Hall (PoC Zone) | Data Hall 1, Suite A
ORD12-ELEC01 | ORD12-FLR01 | ORD12 | Electrical Room | Electrical Switchgear Room 1 (serving PoC zone)
ORD12-MECH01 | ORD12-BLDG01 | ORD12 | Mechanical Plant / Yard | Central Utility Plant / Mechanical Yard
ORD12-GENYD01 | ORD12-BLDG01 | ORD12 | Generator Yard | Standby Generator Yard
LHR10-BLDG01 | LHR10 | LHR10 | Building | London Campus - Building 10
LHR10-FLR01 | LHR10-BLDG01 | LHR10 | Floor | Floor 1 - White Space Level
LHR10-DHPOC | LHR10-FLR01 | LHR10 | Data Hall (PoC Zone) | Data Hall 2, Suite B
LHR10-ELEC01 | LHR10-FLR01 | LHR10 | Electrical Room | Electrical Switchgear Room 1 (serving PoC zone)
LHR10-MECH01 | LHR10-BLDG01 | LHR10 | Mechanical Plant / Yard | Central Utility Plant / Mechanical Yard
LHR10-GENYD01 | LHR10-BLDG01 | LHR10 | Generator Yard | Standby Generator Yard
FRA15-BLDG01 | FRA15 | FRA15 | Building | Hanauer Landstrasse Campus - Building 15
FRA15-FLR01 | FRA15-BLDG01 | FRA15 | Floor | Floor 1 - White Space Level
FRA15-DHPOC | FRA15-FLR01 | FRA15 | Data Hall (PoC Zone) | Data Hall 4, Suite D
FRA15-ELEC01 | FRA15-FLR01 | FRA15 | Electrical Room | Electrical Switchgear Room 1 (serving PoC zone)
FRA15-MECH01 | FRA15-BLDG01 | FRA15 | Mechanical Plant / Yard | Central Utility Plant / Mechanical Yard
FRA15-GENYD01 | FRA15-BLDG01 | FRA15 | Generator Yard | Standby Generator Yard
SIN11-BLDG01 | SIN11 | SIN11 | Building | Loyang Campus - Building 11
SIN11-FLR01 | SIN11-BLDG01 | SIN11 | Floor | Floor 1 - White Space Level
SIN11-DHPOC | SIN11-FLR01 | SIN11 | Data Hall (PoC Zone) | Data Hall 1, Suite A
SIN11-ELEC01 | SIN11-FLR01 | SIN11 | Electrical Room | Electrical Switchgear Room 1 (serving PoC zone)
SIN11-MECH01 | SIN11-BLDG01 | SIN11 | Mechanical Plant / Yard | Central Utility Plant / Mechanical Yard
SIN11-GENYD01 | SIN11-BLDG01 | SIN11 | Generator Yard | Standby Generator Yard
SYD12-BLDG01 | SYD12 | SYD12 | Building | Erskine Park Campus - Building 12
SYD12-FLR01 | SYD12-BLDG01 | SYD12 | Floor | Floor 1 - White Space Level
SYD12-DHPOC | SYD12-FLR01 | SYD12 | Data Hall (PoC Zone) | Data Hall 2, Suite B
SYD12-ELEC01 | SYD12-FLR01 | SYD12 | Electrical Room | Electrical Switchgear Room 1 (serving PoC zone)
SYD12-MECH01 | SYD12-BLDG01 | SYD12 | Mechanical Plant / Yard | Central Utility Plant / Mechanical Yard
SYD12-GENYD01 | SYD12-BLDG01 | SYD12 | Generator Yard | Standby Generator Yard

## Asset Class Master
Class ID | Category | Asset Class Name | SOW Reference | Default Criticality | Recommended Monitoring (SOW Tech) | Maintenance Strategy
MEC-CRAH | Mechanical | CRAH Unit (Computer Room Air Handler) | 3.2 | High | Vibration, Thermal | Condition-Based (Pilot) + Preventive (Baseline)
MEC-CRAC | Mechanical | CRAC Unit (Computer Room Air Conditioner) | 3.2 | High | Vibration, Thermal | Condition-Based (Pilot) + Preventive (Baseline)
MEC-CHIL | Mechanical | Chiller | 3.2 | Critical | Vibration, Thermal, Ultrasound | Condition-Based (Pilot) + Preventive (Baseline)
MEC-COND | Mechanical | Condenser | 3.2 | High | Vibration, Thermal | Condition-Based (Pilot) + Preventive (Baseline)
MEC-CTWR | Mechanical | Cooling Tower | 3.2 | High | Vibration, Thermal | Condition-Based (Pilot) + Preventive (Baseline)
MEC-PUMP | Mechanical | Pump (Chilled / Condenser Water) | 3.2 | High | Vibration, Ultrasound | Condition-Based (Pilot) + Preventive (Baseline)
MEC-AHU | Mechanical | Air Handling Unit (AHU) | 3.2 | Medium | Vibration, Thermal | Condition-Based (Pilot) + Preventive (Baseline)
MEC-DRYC | Mechanical | Dry Cooler | 3.2 | Medium | Vibration, Thermal | Condition-Based (Pilot) + Preventive (Baseline)
ELE-UPS | Electrical | UPS System | 3.2 | Critical | Thermal, Ultrasound | Condition-Based (Pilot) + Preventive (Baseline)
ELE-STS | Electrical | Static Transfer Switch | 3.2 | Critical | Thermal, Ultrasound | Condition-Based (Pilot) + Preventive (Baseline)
ELE-PDU | Electrical | PDU System (Power Distribution Unit) | 3.2 | Critical | Thermal, Ultrasound | Condition-Based (Pilot) + Preventive (Baseline)
ELE-LVSG | Electrical | LV Switchgear | 3.2 | Critical | Thermal, Ultrasound | Condition-Based (Pilot) + Preventive (Baseline)
ELE-HVSG | Electrical | HV Switchgear | 3.2 | Critical | Thermal, Ultrasound | Condition-Based (Pilot) + Preventive (Baseline)
ELE-XFMR | Electrical | Transformer | 3.2 | Critical | Thermal, Ultrasound | Condition-Based (Pilot) + Preventive (Baseline)
ELE-GENA | Electrical | Generator Auxiliary Systems (fuel, starting, control) | 3.2 | High | Thermal, Ultrasound | Condition-Based (Pilot) + Preventive (Baseline)
ELE-GENS | Electrical | Standby Generator Set (parent asset) | Supplementary - not explicitly listed in SOW 3.2 but required to contextualize Generator Auxiliary Systems; recommended addition | Critical | Vibration, Thermal, Ultrasound | Preventive (Baseline) - NFPA 110; PoC monitors auxiliaries only
SUP-BMS | Supporting Systems | BMS Infrastructure (Controllers / Field Panels) | 3.2 | High | Existing Telemetry Only | Preventive (Baseline); data source for PoC
SUP-PMS | Supporting Systems | Power Monitoring System (EPMS) | 3.2 | High | Existing Telemetry Only | Preventive (Baseline); data source for PoC
SUP-BAT | Supporting Systems | Battery Monitoring System | 3.2 | High | Existing Telemetry Only | Preventive (Baseline); data source for PoC
SUP-OT | Supporting Systems | Network-Enabled Operational Technology Asset | 3.2 | Medium | Existing Telemetry Only | Preventive (Baseline); data source for PoC

## Manufacturer Master
Class ID | Asset Class Name | Representative Manufacturers / OEMs (illustrative)
MEC-CRAH | CRAH Unit (Computer Room Air Handler) | Vertiv (Liebert), Stulz, Airedale
MEC-CRAC | CRAC Unit (Computer Room Air Conditioner) | Vertiv (Liebert), Stulz, Airedale
MEC-CHIL | Chiller | Trane, York (Johnson Controls), Carrier
MEC-COND | Condenser | Baltimore Aircoil Company (BAC), EVAPCO, SPX Cooling
MEC-CTWR | Cooling Tower | Baltimore Aircoil Company (BAC), EVAPCO, SPX Cooling
MEC-PUMP | Pump (Chilled / Condenser Water) | Grundfos, Armstrong Fluid Technology, Bell & Gossett
MEC-AHU | Air Handling Unit (AHU) | Trane, Munters, York (Johnson Controls)
MEC-DRYC | Dry Cooler | EVAPCO, Guentner, Baltimore Aircoil Company (BAC)
ELE-UPS | UPS System | Vertiv (Liebert), Schneider Electric (Galaxy), Eaton, Piller
ELE-STS | Static Transfer Switch | Vertiv, ABB, Piller
ELE-PDU | PDU System (Power Distribution Unit) | Vertiv, Schneider Electric, Eaton
ELE-LVSG | LV Switchgear | Schneider Electric, Siemens, Eaton
ELE-HVSG | HV Switchgear | Siemens, ABB, Schneider Electric
ELE-XFMR | Transformer | Siemens, ABB, Schneider Electric
ELE-GENA | Generator Auxiliary Systems (fuel, starting, control) | Caterpillar, Cummins, MTU / Rolls-Royce, Kohler
ELE-GENS | Standby Generator Set (parent asset) | Caterpillar, Cummins, MTU / Rolls-Royce, Kohler
SUP-BMS | BMS Infrastructure (Controllers / Field Panels) | Siemens (Desigo), Schneider Electric (EcoStruxure BMS), Honeywell, Trend Controls
SUP-PMS | Power Monitoring System (EPMS) | Schneider Electric (Power Monitoring Expert), Eaton (Power Xpert), ETAP
SUP-BAT | Battery Monitoring System | Vertiv (Alber / BM3000), EnerSys, Eagle Eye Power Solutions
SUP-OT | Network-Enabled Operational Technology Asset | Moxa, Sensaphone, Panduit (SmartZone)

## Failure Code Master
Failure Code | Monitoring Technology | Failure Mode | SOW Reference
V01 | Vibration | Bearing Wear | 4.2
V02 | Vibration | Misalignment | 4.2
V03 | Vibration | Imbalance | 4.2
V04 | Vibration | Looseness | 4.2
V05 | Vibration | Cavitation | 4.2
V06 | Vibration | Resonance | 4.2
T01 | Thermal | Loose Electrical Connection | 4.3
T02 | Thermal | Overloaded Circuitry | 4.3
T03 | Thermal | Cooling Failure | 4.3
T04 | Thermal | Insulation Degradation | 4.3
T05 | Thermal | Motor Overheating | 4.3
U01 | Ultrasound | Lubrication Breakdown | 4.4
U02 | Ultrasound | Arcing | 4.4
U03 | Ultrasound | Corona Discharge | 4.4
U04 | Ultrasound | Tracking | 4.4
U05 | Ultrasound | Compressed Air Leak | 4.4
U06 | Ultrasound | Damper / Valve Degradation | 4.4

## Asset Register (FASM)
Asset ID | Asset Name | Asset Class | Site ID | Region | Physical Location ID | Asset Criticality Rating | Monitoring Method | Existing Data Source(s) | Additional Sensors (where applicable) | Failure Codes Being Monitored | Manufacturer | Asset Status (Included/Excluded) | Status Rationale
IAD35-CRAH-01 | CRAH Unit (Computer Room Air Handler) 01 - IAD35 | CRAH Unit (Computer Room Air Handler) | IAD35 | NAM | IAD35-DHPOC | High | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; CMMS Maintenance History | Vibration Sensor, Thermal Sensor | V01, V02, V04, T03, T05 | Vertiv (Liebert) | Included | Within approved PoC critical zone / redundancy path
IAD35-CRAC-01 | CRAC Unit (Computer Room Air Conditioner) 01 - IAD35 | CRAC Unit (Computer Room Air Conditioner) | IAD35 | NAM | IAD35-DHPOC | High | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; CMMS Maintenance History | Vibration Sensor, Thermal Sensor | V01, V02, V04, T03, T05 | Vertiv (Liebert) | Included | Within approved PoC critical zone / redundancy path
IAD35-CHIL-01 | Chiller 01 - IAD35 | Chiller | IAD35 | NAM | IAD35-MECH01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; OEM Monitoring Platform; CMMS Maintenance History | Vibration Sensor, Thermal Sensor, Ultrasound Sensor | V01, V02, V03, V05, U01, T03 | Trane | Included | Within approved PoC critical zone / redundancy path
IAD35-COND-01 | Condenser 01 - IAD35 | Condenser | IAD35 | NAM | IAD35-MECH01 | High | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; CMMS Maintenance History | Vibration Sensor, Thermal Sensor | V01, V04, T03 | Baltimore Aircoil Company (BAC) | Included | Within approved PoC critical zone / redundancy path
IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Cooling Tower | IAD35 | NAM | IAD35-MECH01 | High | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; CMMS Maintenance History | Vibration Sensor, Thermal Sensor | V01, V03, V06, T03 | Baltimore Aircoil Company (BAC) | Included | Within approved PoC critical zone / redundancy path
IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Pump (Chilled / Condenser Water) | IAD35 | NAM | IAD35-MECH01 | High | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; CMMS Maintenance History | Vibration Sensor, Ultrasound Sensor | V01, V02, V03, V05, U01 | Grundfos | Included | Within approved PoC critical zone / redundancy path
IAD35-AHU-01 | Air Handling Unit (AHU) 01 - IAD35 | Air Handling Unit (AHU) | IAD35 | NAM | IAD35-DHPOC | Medium | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; CMMS Maintenance History | Vibration Sensor, Thermal Sensor | V01, V04, T03, T05 | Trane | Included | Within approved PoC critical zone / redundancy path
IAD35-DRYC-01 | Dry Cooler 01 - IAD35 | Dry Cooler | IAD35 | NAM | IAD35-MECH01 | Medium | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; CMMS Maintenance History | Vibration Sensor, Thermal Sensor | V01, V04, T03 | EVAPCO | Excluded | Outside approved PoC critical zone boundary - deferred to future phase
ORD12-COND-01 | Condenser 01 - ORD12 | Condenser | ORD12 | NAM | ORD12-MECH01 | High | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; CMMS Maintenance History | Vibration Sensor, Thermal Sensor | V01, V04, T03 | EVAPCO | Included | Within approved PoC critical zone / redundancy path
ORD12-CTWR-01 | Cooling Tower 01 - ORD12 | Cooling Tower | ORD12 | NAM | ORD12-MECH01 | High | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; CMMS Maintenance History | Vibration Sensor, Thermal Sensor | V01, V03, V06, T03 | EVAPCO | Included | Within approved PoC critical zone / redundancy path
ORD12-PUMP-01 | Pump (Chilled / Condenser Water) 01 - ORD12 | Pump (Chilled / Condenser Water) | ORD12 | NAM | ORD12-MECH01 | High | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; CMMS Maintenance History | Vibration Sensor, Ultrasound Sensor | V01, V02, V03, V05, U01 | Armstrong Fluid Technology | Included | Within approved PoC critical zone / redundancy path
ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Air Handling Unit (AHU) | ORD12 | NAM | ORD12-DHPOC | Medium | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; CMMS Maintenance History | Vibration Sensor, Thermal Sensor | V01, V04, T03, T05 | Munters | Included | Within approved PoC critical zone / redundancy path
ORD12-DRYC-01 | Dry Cooler 01 - ORD12 | Dry Cooler | ORD12 | NAM | ORD12-MECH01 | Medium | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; CMMS Maintenance History | Vibration Sensor, Thermal Sensor | V01, V04, T03 | Guentner | Included | Within approved PoC critical zone / redundancy path
ORD12-UPS-01 | UPS System 01 - ORD12 | UPS System | ORD12 | NAM | ORD12-ELEC01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | EPMS; DCIM; OEM Monitoring Platform; Battery Monitoring System; CMMS Maintenance History | Thermal Sensor, Ultrasound Sensor | T01, T02, T04, U02, U03 | Schneider Electric (Galaxy) | Included | Within approved PoC critical zone / redundancy path
ORD12-STS-01 | Static Transfer Switch 01 - ORD12 | Static Transfer Switch | ORD12 | NAM | ORD12-ELEC01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | EPMS; DCIM; CMMS Maintenance History | Thermal Sensor, Ultrasound Sensor | T01, U02, U03, U04 | ABB | Included | Within approved PoC critical zone / redundancy path
ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | PDU System (Power Distribution Unit) | ORD12 | NAM | ORD12-ELEC01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | EPMS; DCIM; CMMS Maintenance History | Thermal Sensor, Ultrasound Sensor | T01, T02, U02 | Schneider Electric | Included | Within approved PoC critical zone / redundancy path
LHR10-AHU-01 | Air Handling Unit (AHU) 01 - LHR10 | Air Handling Unit (AHU) | LHR10 | EMEA | LHR10-DHPOC | Medium | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; CMMS Maintenance History | Vibration Sensor, Thermal Sensor | V01, V04, T03, T05 | York (Johnson Controls) | Included | Within approved PoC critical zone / redundancy path
LHR10-DRYC-01 | Dry Cooler 01 - LHR10 | Dry Cooler | LHR10 | EMEA | LHR10-MECH01 | Medium | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; CMMS Maintenance History | Vibration Sensor, Thermal Sensor | V01, V04, T03 | Baltimore Aircoil Company (BAC) | Included | Within approved PoC critical zone / redundancy path
LHR10-UPS-01 | UPS System 01 - LHR10 | UPS System | LHR10 | EMEA | LHR10-ELEC01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | EPMS; DCIM; OEM Monitoring Platform; Battery Monitoring System; CMMS Maintenance History | Thermal Sensor, Ultrasound Sensor | T01, T02, T04, U02, U03 | Eaton | Included | Within approved PoC critical zone / redundancy path
LHR10-STS-01 | Static Transfer Switch 01 - LHR10 | Static Transfer Switch | LHR10 | EMEA | LHR10-ELEC01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | EPMS; DCIM; CMMS Maintenance History | Thermal Sensor, Ultrasound Sensor | T01, U02, U03, U04 | Piller | Included | Within approved PoC critical zone / redundancy path
LHR10-PDU-01 | PDU System (Power Distribution Unit) 01 - LHR10 | PDU System (Power Distribution Unit) | LHR10 | EMEA | LHR10-ELEC01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | EPMS; DCIM; CMMS Maintenance History | Thermal Sensor, Ultrasound Sensor | T01, T02, U02 | Eaton | Included | Within approved PoC critical zone / redundancy path
LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | LV Switchgear | LHR10 | EMEA | LHR10-ELEC01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | EPMS; DCIM; CMMS Maintenance History; Incident History | Thermal Sensor, Ultrasound Sensor | T01, T02, U02, U03, U04 | Eaton | Included | Within approved PoC critical zone / redundancy path
LHR10-HVSG-01 | HV Switchgear 01 - LHR10 | HV Switchgear | LHR10 | EMEA | LHR10-ELEC01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | EPMS; DCIM; CMMS Maintenance History; Incident History | Thermal Sensor, Ultrasound Sensor | T01, U02, U03, U04 | Schneider Electric | Included | Within approved PoC critical zone / redundancy path
LHR10-XFMR-01 | Transformer 01 - LHR10 | Transformer | LHR10 | EMEA | LHR10-ELEC01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | EPMS; DCIM; CMMS Maintenance History; Incident History | Thermal Sensor, Ultrasound Sensor | T01, T02, T04, U02, U03 | Schneider Electric | Included | Within approved PoC critical zone / redundancy path
FRA15-STS-01 | Static Transfer Switch 01 - FRA15 | Static Transfer Switch | FRA15 | EMEA | FRA15-ELEC01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | EPMS; DCIM; CMMS Maintenance History | Thermal Sensor, Ultrasound Sensor | T01, U02, U03, U04 | Vertiv | Included | Within approved PoC critical zone / redundancy path
FRA15-PDU-01 | PDU System (Power Distribution Unit) 01 - FRA15 | PDU System (Power Distribution Unit) | FRA15 | EMEA | FRA15-ELEC01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | EPMS; DCIM; CMMS Maintenance History | Thermal Sensor, Ultrasound Sensor | T01, T02, U02 | Vertiv | Included | Within approved PoC critical zone / redundancy path
FRA15-LVSG-01 | LV Switchgear 01 - FRA15 | LV Switchgear | FRA15 | EMEA | FRA15-ELEC01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | EPMS; DCIM; CMMS Maintenance History; Incident History | Thermal Sensor, Ultrasound Sensor | T01, T02, U02, U03, U04 | Schneider Electric | Included | Within approved PoC critical zone / redundancy path
FRA15-HVSG-01 | HV Switchgear 01 - FRA15 | HV Switchgear | FRA15 | EMEA | FRA15-ELEC01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | EPMS; DCIM; CMMS Maintenance History; Incident History | Thermal Sensor, Ultrasound Sensor | T01, U02, U03, U04 | Siemens | Included | Within approved PoC critical zone / redundancy path
FRA15-XFMR-01 | Transformer 01 - FRA15 | Transformer | FRA15 | EMEA | FRA15-ELEC01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | EPMS; DCIM; CMMS Maintenance History; Incident History | Thermal Sensor, Ultrasound Sensor | T01, T02, T04, U02, U03 | Siemens | Included | Within approved PoC critical zone / redundancy path
FRA15-GENA-01 | Generator Auxiliary Systems (fuel, starting, control) 01 - FRA15 | Generator Auxiliary Systems (fuel, starting, control) | FRA15 | EMEA | FRA15-GENYD01 | High | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; EPMS; OEM Monitoring Platform; CMMS Maintenance History | Thermal Sensor, Ultrasound Sensor | T05, U01, U05 | Kohler | Included | Within approved PoC critical zone / redundancy path
FRA15-GENS-01 | Standby Generator Set (parent asset) 01 - FRA15 | Standby Generator Set (parent asset) | FRA15 | EMEA | FRA15-GENYD01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; EPMS; OEM Monitoring Platform; CMMS Maintenance History | Vibration Sensor, Thermal Sensor, Ultrasound Sensor | V01, V02, V04, T05, U01 | Kohler | Included | Within approved PoC critical zone / redundancy path
FRA15-BMS-01 | BMS Infrastructure (Controllers / Field Panels) 01 - FRA15 | BMS Infrastructure (Controllers / Field Panels) | FRA15 | EMEA | FRA15-ELEC01 | High | Existing Telemetry (BMS/EPMS/DCIM) | BMS; Asset Registry Information | None (existing telemetry only) | N/A (telemetry-only asset) | Trend Controls | Included | Within approved PoC critical zone / redundancy path
SIN11-HVSG-01 | HV Switchgear 01 - SIN11 | HV Switchgear | SIN11 | APAC | SIN11-ELEC01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | EPMS; DCIM; CMMS Maintenance History; Incident History | Thermal Sensor, Ultrasound Sensor | T01, U02, U03, U04 | ABB | Included | Within approved PoC critical zone / redundancy path
SIN11-XFMR-01 | Transformer 01 - SIN11 | Transformer | SIN11 | APAC | SIN11-ELEC01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | EPMS; DCIM; CMMS Maintenance History; Incident History | Thermal Sensor, Ultrasound Sensor | T01, T02, T04, U02, U03 | ABB | Included | Within approved PoC critical zone / redundancy path
SIN11-GENA-01 | Generator Auxiliary Systems (fuel, starting, control) 01 - SIN11 | Generator Auxiliary Systems (fuel, starting, control) | SIN11 | APAC | SIN11-GENYD01 | High | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; EPMS; OEM Monitoring Platform; CMMS Maintenance History | Thermal Sensor, Ultrasound Sensor | T05, U01, U05 | Caterpillar | Included | Within approved PoC critical zone / redundancy path
SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Standby Generator Set (parent asset) | SIN11 | APAC | SIN11-GENYD01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; EPMS; OEM Monitoring Platform; CMMS Maintenance History | Vibration Sensor, Thermal Sensor, Ultrasound Sensor | V01, V02, V04, T05, U01 | Caterpillar | Included | Within approved PoC critical zone / redundancy path
SIN11-BMS-01 | BMS Infrastructure (Controllers / Field Panels) 01 - SIN11 | BMS Infrastructure (Controllers / Field Panels) | SIN11 | APAC | SIN11-ELEC01 | High | Existing Telemetry (BMS/EPMS/DCIM) | BMS; Asset Registry Information | None (existing telemetry only) | N/A (telemetry-only asset) | Siemens (Desigo) | Included | Within approved PoC critical zone / redundancy path
SIN11-PMS-01 | Power Monitoring System (EPMS) 01 - SIN11 | Power Monitoring System (EPMS) | SIN11 | APAC | SIN11-ELEC01 | High | Existing Telemetry (BMS/EPMS/DCIM) | EPMS; Asset Registry Information | None (existing telemetry only) | N/A (telemetry-only asset) | Eaton (Power Xpert) | Included | Within approved PoC critical zone / redundancy path
SIN11-BAT-01 | Battery Monitoring System 01 - SIN11 | Battery Monitoring System | SIN11 | APAC | SIN11-ELEC01 | High | Existing Telemetry (BMS/EPMS/DCIM) | Battery Monitoring System; EPMS; Asset Registry Information | None (existing telemetry only) | N/A (telemetry-only asset) | EnerSys | Included | Within approved PoC critical zone / redundancy path
SIN11-OT-01 | Network-Enabled Operational Technology Asset 01 - SIN11 | Network-Enabled Operational Technology Asset | SIN11 | APAC | SIN11-DHPOC | Medium | Existing Telemetry (BMS/EPMS/DCIM) | DCIM; Asset Registry Information | None (existing telemetry only) | N/A (telemetry-only asset) | Sensaphone | Excluded | Outside approved PoC critical zone boundary - deferred to future phase
SYD12-GENS-01 | Standby Generator Set (parent asset) 01 - SYD12 | Standby Generator Set (parent asset) | SYD12 | APAC | SYD12-GENYD01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; EPMS; OEM Monitoring Platform; CMMS Maintenance History | Vibration Sensor, Thermal Sensor, Ultrasound Sensor | V01, V02, V04, T05, U01 | Cummins | Included | Within approved PoC critical zone / redundancy path
SYD12-BMS-01 | BMS Infrastructure (Controllers / Field Panels) 01 - SYD12 | BMS Infrastructure (Controllers / Field Panels) | SYD12 | APAC | SYD12-ELEC01 | High | Existing Telemetry (BMS/EPMS/DCIM) | BMS; Asset Registry Information | None (existing telemetry only) | N/A (telemetry-only asset) | Schneider Electric (EcoStruxure BMS) | Included | Within approved PoC critical zone / redundancy path
SYD12-PMS-01 | Power Monitoring System (EPMS) 01 - SYD12 | Power Monitoring System (EPMS) | SYD12 | APAC | SYD12-ELEC01 | High | Existing Telemetry (BMS/EPMS/DCIM) | EPMS; Asset Registry Information | None (existing telemetry only) | N/A (telemetry-only asset) | ETAP | Included | Within approved PoC critical zone / redundancy path
SYD12-BAT-01 | Battery Monitoring System 01 - SYD12 | Battery Monitoring System | SYD12 | APAC | SYD12-ELEC01 | High | Existing Telemetry (BMS/EPMS/DCIM) | Battery Monitoring System; EPMS; Asset Registry Information | None (existing telemetry only) | N/A (telemetry-only asset) | Eagle Eye Power Solutions | Included | Within approved PoC critical zone / redundancy path
SYD12-OT-01 | Network-Enabled Operational Technology Asset 01 - SYD12 | Network-Enabled Operational Technology Asset | SYD12 | APAC | SYD12-DHPOC | Medium | Existing Telemetry (BMS/EPMS/DCIM) | DCIM; Asset Registry Information | None (existing telemetry only) | N/A (telemetry-only asset) | Panduit (SmartZone) | Included | Within approved PoC critical zone / redundancy path
SYD12-CRAH-01 | CRAH Unit (Computer Room Air Handler) 01 - SYD12 | CRAH Unit (Computer Room Air Handler) | SYD12 | APAC | SYD12-DHPOC | High | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; CMMS Maintenance History | Vibration Sensor, Thermal Sensor | V01, V02, V04, T03, T05 | Airedale | Included | Within approved PoC critical zone / redundancy path
SYD12-CRAC-01 | CRAC Unit (Computer Room Air Conditioner) 01 - SYD12 | CRAC Unit (Computer Room Air Conditioner) | SYD12 | APAC | SYD12-DHPOC | High | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; CMMS Maintenance History | Vibration Sensor, Thermal Sensor | V01, V02, V04, T03, T05 | Airedale | Included | Within approved PoC critical zone / redundancy path
SYD12-CHIL-01 | Chiller 01 - SYD12 | Chiller | SYD12 | APAC | SYD12-MECH01 | Critical | Existing Telemetry (BMS/EPMS/DCIM) + New Condition Monitoring Sensors | BMS; DCIM; OEM Monitoring Platform; CMMS Maintenance History | Vibration Sensor, Thermal Sensor, Ultrasound Sensor | V01, V02, V03, V05, U01, T03 | Carrier | Included | Within approved PoC critical zone / redundancy path

## Criticality Rating Matrix
Rating | Tier | Redundancy Impact | Business Impact | Response SLA
Critical | Tier 1 | Loss reduces a live path to N or creates a single point of failure (SPOF) on the critical power/cooling chain. | Direct risk to customer-facing IT load; potential SLA breach / outage. | Immediate (<15 min) engineering response
High | Tier 2 | Asset is an N+1 or redundant leg; loss reduces redundancy margin but does not immediately drop a live path. | Elevated risk if a second, unrelated failure occurs before repair. | <1 hour engineering response
Medium | Tier 3 | Supporting or monitoring asset; typically redundant and off the direct critical path. | Localized or comfort-cooling impact; no immediate customer-facing risk. | <4 hours / next business day
Low | Tier 4 | Non-critical or informational asset. | No material operational impact. | Standard SLA / scheduled

## Data Source & System Master
System ID | System Name | System Type | Representative Vendor/Platform | Protocol | Typical Data Points | Scope | Sample Data Location
SYS-BMS | Building Management System (BMS) | Existing OT Platform | Siemens Desigo / Schneider EcoStruxure BMS (site-dependent) | BACnet / Modbus | Temperature, humidity, airflow, valve/damper position, alarms | All 6 PoC sites | BMS Data Sample (Transactional workbook)
SYS-EPMS | Electrical Power Monitoring System (EPMS) | Existing OT Platform | Schneider Power Monitoring Expert / Eaton Power Xpert (site-dependent) | Modbus TCP / IEC 61850 | Voltage, current, power factor, breaker status, protective relay events | All 6 PoC sites | EPMS Data Sample (Transactional workbook)
SYS-DCIM | Data Center Infrastructure Management (DCIM) | Existing OT Platform | Site DCIM platform (vendor confirmed during Section 5.1 Solution Design) | API / SNMP / BACnet | Capacity, PUE, asset inventory, environmental trend history | All 6 PoC sites | DCIM Data Sample (Transactional workbook)
SYS-OEM | OEM Monitoring Platform(s) | Existing Vendor Platform | e.g., Vertiv LIFE Services, Caterpillar VisionLink (asset-dependent) | Cloud API | OEM-specific health/alarm data for UPS, generator, chiller fleets | Site- and OEM-dependent | OEM Monitoring Sample (Transactional workbook)
SYS-BAT | Battery Monitoring System | Existing OT Platform | Vertiv Alber / EnerSys (site-dependent) | Modbus / Vendor API | Cell voltage, internal resistance, temperature, state of health | Sites with monitored VRLA/Li-ion strings | Battery Monitoring Sample (Transactional workbook)
SYS-CMMS | CMMS Maintenance History | Existing Enterprise System | Digital Realty enterprise CMMS | Flat file / API export | Work order history, PM compliance, failure/incident records | All 6 PoC sites | Work Orders + PM Compliance Log (Transactional workbook)
SYS-AST | Asset Registry Information | Existing Enterprise System | Digital Realty enterprise asset register / CMMS asset module | Flat file / API export | Asset ID, class, manufacturer, location, criticality, install data | All 6 PoC sites | Asset Register - FASM (Master Data workbook)
SYS-INC | Incident History | Existing Enterprise System | Digital Realty incident/event management system | Flat file / API export | Incident date, asset, root cause, downtime, customer impact | All 6 PoC sites | Incident History - Baseline (Transactional workbook)
SYS-VIB | Vibration Sensor Platform (New - PoC) | New Condition Monitoring Technology | Technology partner selected under Section 5.1 Solution Design | Wireless (LoRaWAN/BLE) to Gateway | Vibration velocity/acceleration spectra, bearing condition indicators | PoC critical zone only, per site | Condition Monitoring Readings (Transactional workbook)
SYS-THM | Thermal Sensor Platform (New - PoC) | New Condition Monitoring Technology | Technology partner selected under Section 5.1 Solution Design | Fixed IR camera / spot sensor, IP network | Surface/connection temperature, thermal trend and delta-T alarms | PoC critical zone only, per site | Condition Monitoring Readings (Transactional workbook)
SYS-USN | Ultrasound Sensor Platform (New - PoC) | New Condition Monitoring Technology | Technology partner selected under Section 5.1 Solution Design | Airborne/contact ultrasound, wireless to Gateway | Arcing/corona/tracking acoustic signatures, air/gas leak indicators | PoC critical zone only, per site | Condition Monitoring Readings (Transactional workbook)

## Governance & Stakeholder Master
Stakeholder / Role | RACI (PoC Governance) | Typical Review Cadence | Core Responsibility
Global Technical Operations | Accountable | Monthly Executive Update | Owns global FSM strategy, scale-up decision, and cross-region standardization.
Regional Operations | Responsible | Weekly / Biweekly Review | Coordinates PoC execution and resourcing across EMEA / NAM / APAC sites.
Site Leadership | Accountable (Site) | Weekly / Biweekly Review | Approves site access, change windows, and site-level risk acceptance.
Site Engineering | Responsible | Weekly / Biweekly Review | Executes physical inspections, validates alerts, and performs maintenance actions.
Reliability Engineering | Consulted | Weekly / Biweekly Review | Defines asset criticality, RCM failure modes, and correlates findings to reliability KPIs.
Asset Management | Consulted | Monthly Executive Update | Maintains asset registry, manufacturer/model data, and lifecycle records.
IT / OT Teams | Responsible | Ad hoc / Change Windows | Provides network, cybersecurity review, and integration support for sensor/gateway deployment.
Vendor Partners | Responsible (Delivery) | Weekly / Biweekly Review | Installs and commissions sensors, operates analytics platform, and reports findings.

## PM Task Library (Baseline)
Task ID | Class ID | Asset Class | PM Task | Frequency | Standard / Reference | Affected by PoC?
PM-CRAH-01 | MEC-CRAH | CRAH Unit (Computer Room Air Handler) | Filter inspection/replacement | Monthly | ASHRAE TC 9.9 | No - preserved per SOW 2.2
PM-CRAH-02 | MEC-CRAH | CRAH Unit (Computer Room Air Handler) | Belt, bearing & coil inspection | Quarterly | OEM / ASHRAE TC 9.9 | No - preserved per SOW 2.2
PM-CRAC-01 | MEC-CRAC | CRAC Unit (Computer Room Air Conditioner) | Filter inspection/replacement | Monthly | ASHRAE TC 9.9 | No - preserved per SOW 2.2
PM-CHIL-01 | MEC-CHIL | Chiller | Full mechanical/refrigeration PM & oil analysis | Quarterly | OEM / ASHRAE | No - preserved per SOW 2.2
PM-CHIL-02 | MEC-CHIL | Chiller | Annual eddy-current tube inspection | Annual | OEM / ASHRAE | No - preserved per SOW 2.2
PM-COND-01 | MEC-COND | Condenser | Coil cleaning & fan inspection | Quarterly | OEM | No - preserved per SOW 2.2
PM-CTWR-01 | MEC-CTWR | Cooling Tower | Basin cleaning & water treatment check | Monthly | ASHRAE Legionella Std 188 | No - preserved per SOW 2.2
PM-PUMP-01 | MEC-PUMP | Pump (Chilled / Condenser Water) | Seal/bearing inspection & alignment check | Quarterly | OEM | No - preserved per SOW 2.2
PM-AHU-01 | MEC-AHU | Air Handling Unit (AHU) | Filter & belt inspection | Monthly | ASHRAE TC 9.9 | No - preserved per SOW 2.2
PM-DRYC-01 | MEC-DRYC | Dry Cooler | Coil cleaning & fan inspection | Quarterly | OEM | No - preserved per SOW 2.2
PM-UPS-01 | ELE-UPS | UPS System | UPS module PM inspection | Quarterly | NFPA 70B / OEM | No - preserved per SOW 2.2
PM-UPS-02 | ELE-UPS | UPS System | Battery string load/impedance test | Annual | NFPA 111 / IEEE 450 | No - preserved per SOW 2.2
PM-STS-01 | ELE-STS | Static Transfer Switch | Static switch functional transfer test | Annual | OEM | No - preserved per SOW 2.2
PM-PDU-01 | ELE-PDU | PDU System (Power Distribution Unit) | PDU thermographic scan & torque check | Annual | NFPA 70B | No - preserved per SOW 2.2
PM-LVSG-01 | ELE-LVSG | LV Switchgear | Switchgear IR thermography scan | Annual | NFPA 70B | No - preserved per SOW 2.2
PM-LVSG-02 | ELE-LVSG | LV Switchgear | Breaker maintenance & torque verification | Every 3 Years | NFPA 70B / NETA | No - preserved per SOW 2.2
PM-HVSG-01 | ELE-HVSG | HV Switchgear | HV switchgear inspection & IR scan | Annual | NFPA 70E / NETA | No - preserved per SOW 2.2
PM-XFMR-01 | ELE-XFMR | Transformer | Transformer oil sampling & IR scan | Annual | IEEE C57.104 / NFPA 70B | No - preserved per SOW 2.2
PM-GENA-01 | ELE-GENA | Generator Auxiliary Systems (fuel, starting, control) | Fuel system & starting battery inspection | Monthly | NFPA 110 | No - preserved per SOW 2.2
PM-GENS-01 | ELE-GENS | Standby Generator Set (parent asset) | No-load exercise run | Weekly | NFPA 110 | No - preserved per SOW 2.2
PM-GENS-02 | ELE-GENS | Standby Generator Set (parent asset) | Full load bank test | Annual | NFPA 110 | No - preserved per SOW 2.2
PM-BMS-01 | SUP-BMS | BMS Infrastructure (Controllers / Field Panels) | Controller/sensor calibration check | Annual | OEM | No - preserved per SOW 2.2
PM-PMS-01 | SUP-PMS | Power Monitoring System (EPMS) | Meter/relay calibration verification | Annual | OEM / NETA | No - preserved per SOW 2.2
PM-BAT-01 | SUP-BAT | Battery Monitoring System | Monitoring system self-test & sensor check | Quarterly | OEM | No - preserved per SOW 2.2
PM-OT-01 | SUP-OT | Network-Enabled Operational Technology Asset | Firmware/patch and connectivity check | Quarterly | Digital Realty IT/OT Policy | No - preserved per SOW 2.2

## KPI Master
KPI ID | Group | KPI | Target (per SOW Sec. 8) | Definition | Primary Data Source
KPI-T01 | Technical | Sensor Availability | ~90-100% | % of deployed sensors reporting data as expected over the measurement period. | Sensor Platform / Dashboard
KPI-T02 | Technical | Data Acquisition Reliability | ~90-100% | % of expected data points successfully collected from BMS/EPMS/DCIM/sensors without gaps. | Analytics Platform
KPI-T03 | Technical | Alert Accuracy | ~70-80% | % of generated alerts confirmed as valid by engineering review / physical inspection. | Alert & Anomaly Register
KPI-T04 | Technical | False Positive Rate | ~10-20% | % of generated alerts closed as not indicative of a real condition. | Alert & Anomaly Register
KPI-T05 | Technical | Dashboard Availability | ~90-100% | % uptime of the centralized monitoring dashboard during the PoC period. | Analytics Platform
KPI-O01 | Operational | Early Fault Detection | Demonstrated | Evidence that condition monitoring detected degradation ahead of traditional PM/inspection. | Maintenance Correlation Log
KPI-O02 | Operational | Reduced Unplanned Maintenance Risk | Demonstrated | Evidence of reduced unplanned-outage risk attributable to condition-based intervention. | Work Orders / Incident History
KPI-O03 | Operational | Maintenance Optimization Opportunities | Demonstrated | Identified opportunities to adjust maintenance frequency/scope based on actual asset condition. | Maintenance Correlation Log
KPI-O04 | Operational | Condition-Based Interventions | Demonstrated | Count and outcome of maintenance actions triggered by condition data rather than calendar. | Work Orders
KPI-O05 | Operational | Business Case for Scale | Developed | Documented ROI / benefits-realization case supporting a global deployment decision. | Final PoC Report