## Read Me
Digital Realty - Future State Maintenance (FSM) PoC Transactional Data Workbook
Purpose
This workbook contains the illustrative transactional records that the FSM PoC will generate once live: sample integrated data pulled from every SOW Section 4.1 existing system (BMS, EPMS, DCIM, OEM monitoring platforms, Battery Monitoring System, CMMS, asset registry, incident history) alongside the new vibration/thermal/ultrasound condition monitoring, the resulting alerts, work orders, correlation findings, a live KPI dashboard, a benefits realization assessment, PM compliance, weekly health reports, baseline incident history, the risk register, and the two readiness checklists required as SOW deliverables.
Important assumption
All dates, readings, alerts, work orders, and log entries in this workbook are ILLUSTRATIVE sample data intended to demonstrate the transactional data model and the SOW Section 7.2 response workflow (Alert generated -> Engineering review -> Condition validation -> Maintenance action determination -> Work order execution -> Outcome recorded -> Feedback incorporated into analytics). They are not real Digital Realty operational records. IDs cross-reference the companion 'DigitalRealty_FSM_PoC_Master_Data.xlsx' workbook (Asset Register, PM Task Library, Site Master).
How this aligns to the SOW
• 'BMS Data Sample', 'EPMS Data Sample', 'DCIM Data Sample', 'OEM Monitoring Sample', and 'Battery Monitoring Sample' give every SOW Section 4.1 existing data source its own illustrative integrated feed - not just a catalog entry - and several rows are deliberately timestamped to corroborate the same real-world events as the Alert & Anomaly Register (e.g., the EPMS ground-fault pre-alarm and harmonic distortion readings that precede ALT-0003 by minutes, or the OEM platform's own diagnostic flag on ALT-0002), demonstrating multi-source correlation per SOW Section 6.1.
• 'Alert & Anomaly Register' and 'Work Orders' implement the Section 7.2 Response Workflow end to end, including a false-positive example so Alert Accuracy / False Positive Rate KPIs (Section 8) are computable.
• 'KPI Dashboard (Actuals)' computes all 10 Section 8 Technical and Operational KPIs live with spreadsheet formulas (AVERAGE/COUNTIF/COUNTIFS) against the sheets above, rather than static text, so it recalculates automatically as real PoC data is added - the analytics deliverable behind the Section 2.1 KPI Monitoring and Performance Assessment activities.
• 'Benefits Realization Assessment' is the named Section 9 deliverable and is the evidence base behind KPI-O05 'Business Case for Scale'.
• 'Maintenance Correlation Log' is the named SOW deliverable correlating detected anomalies with physical inspections and maintenance findings (Sections 2.1, 9).
• 'PM Compliance Log' shows the existing calendar-based PM (from the Master Data 'PM Task Library') continuing to run unchanged in parallel, per SOW Section 2.2.
• 'Weekly Health Report Log' reflects the Section 2.1 cadence: weekly during the initial period, moving to biweekly as the PoC progresses, and now carries all three Technical KPI inputs (Sensor Availability, Data Acquisition Reliability, Dashboard Availability) as live percentages.
• 'Incident History (Baseline)' addresses the Section 10 risk 'Limited historical data' by establishing baseline operating profiles before PoC monitoring begins.
• 'Risk-Assumption-Dependency Reg' combines the Section 10 risk table with the Section 5.2 requirement for an Assumptions, Dependencies, and Risk Register.
• 'Site Readiness Checklist' and 'Technical Prereq Checklist' are named Section 5.2 deliverables, structured against its prerequisite categories.
Companion file
See 'DigitalRealty_FSM_PoC_Master_Data.xlsx' for Site, Location, Asset Class, Manufacturer, Failure Code, Asset Register, Criticality, Data Source/System (with a 'Sample Data Location' column pointing back into this workbook), Stakeholder, PM Task, and KPI master tables that these transactions reference.
Workbook map
• 1. Work Orders - sample work orders spanning condition-based, calendar, and reactive triggers.
• 2. Alert & Anomaly Register - sample alerts with severity, validation outcome, and linked work orders.
• 3. Condition Monitoring Readings - sample vibration/thermal/ultrasound readings feeding the alerts.
• 4. BMS Data Sample - sample Building Management System telemetry (SOW 4.1).
• 5. EPMS Data Sample - sample Electrical Power Monitoring System telemetry (SOW 4.1).
• 6. DCIM Data Sample - sample Data Center Infrastructure Management metrics (SOW 4.1).
• 7. OEM Monitoring Sample - sample OEM monitoring-platform health/alarm data (SOW 4.1).
• 8. Battery Monitoring Sample - sample Battery Monitoring System readings (SOW 4.1).
• 9. Maintenance Correlation Log - inspection/maintenance findings correlated to each alert.
• 10. KPI Dashboard (Actuals) - all 10 SOW Section 8 KPIs computed live from the sheets above.
• 11. Benefits Realization Assessment - named SOW Section 9 deliverable.
• 12. PM Compliance Log - baseline calendar PM schedule vs. completion status.
• 13. Weekly Health Report Log - governance reporting cadence per SOW 2.1.
• 14. Incident History (Baseline) - pre-PoC historical incidents for baseline comparison.
• 15. Risk-Assumption-Dependency Reg - SOW 5.2 / Section 10 deliverable.
• 16. Site Readiness Checklist - SOW 5.2 deliverable.
• 17. Technical Prereq Checklist - SOW 5.2 deliverable.

## Work Orders
Work Order ID | Date Raised | Asset ID | Site ID | Trigger Source | Linked Alert ID | Priority | Description | Maintenance Action / Finding | Assigned To | Status | Date Completed | Outcome | Feedback to Analytics (Step 7)
WO-1001 | 2026-09-16 | IAD35-PUMP-01 | IAD35 | Condition-Based Alert | ALT-0001 | High | Inspect condenser water pump for imbalance; rebalance/replace impeller as required. | Physical inspection confirmed impeller wear; pump rebalanced under redundant-path MOP. | Site Engineering | Completed | 2026-09-18 | Vibration returned to baseline; no cooling redundancy impact. | Confirms vibration sensing detects impeller wear ahead of quarterly PM interval.
WO-1002 | 2026-09-20 | ORD12-UPS-01 | ORD12 | Condition-Based Alert | ALT-0002 | Critical | Investigate and correct thermal hot spot at UPS input terminal. | De-energized redundant module per MOP; found and corrected a loose input lug connection. | Site Engineering + Electrical Vendor | Completed | 2026-09-21 | Thermal signature normalized; avoided potential connection failure on critical load path. | Add torque-check/thermal-scan step to UPS quarterly PM checklist.
WO-1003 | 2026-09-27 | LHR10-LVSG-01 | LHR10 | Condition-Based Alert | ALT-0003 | Critical | Investigate ultrasonic arcing signature at LV switchgear breaker connection. | Isolated redundant breaker per MOP; resurfaced degraded contact; verified with follow-up ultrasound scan. | Site Engineering + Switchgear OEM | Completed | 2026-09-29 | Arcing signature eliminated; avoided potential unplanned breaker trip. | Validates ultrasound as an earlier leading indicator than annual IR thermography for switchgear.
WO-1004 | 2026-10-02 | FRA15-XFMR-01 | FRA15 | Condition-Based Alert | ALT-0004 | High | Pull oil sample from transformer for dissolved-gas analysis (DGA). | Sample pulled and submitted to accredited lab; results pending. | Site Engineering | In Progress |  | Pending lab result. | Pending - correlation log to be updated on DGA result.
WO-1005 | 2026-10-06 | SIN11-GENS-01 | SIN11 | Condition-Based Alert | ALT-0005 | Medium | Correct minor coupling misalignment on standby generator set. | Alignment corrected during scheduled weekly no-load exercise run (no extra outage window required). | Site Engineering | Completed | 2026-10-06 | Vibration within normal limits on next exercise run. | Confirms condition data can be actioned inside existing PM windows at no added risk.
WO-1006 | 2026-10-14 | IAD35-CRAH-01 | IAD35 | Condition-Based Alert | ALT-0007 | Medium | Investigate elevated CRAH fan motor temperature. | Inspected drive belt; found slippage; adjusted tension. | Site Engineering | Completed | 2026-10-14 | Motor temperature normalized. | Minor finding; no change to PM interval recommended.
WO-1007 | 2026-10-01 | LHR10-UPS-01 | LHR10 | Calendar PM (PM-UPS-02) | N/A | Scheduled | Annual UPS battery string load/impedance test. | Load/impedance test performed on all strings per IEEE 450. | Site Engineering + Battery Vendor | Completed | 2026-10-01 | All strings within OEM specification. | Baseline PM unaffected by PoC, per SOW Section 2.2.
WO-1008 | 2026-09-24 | ORD12-DRYC-01 | ORD12 | Reactive (Operator Reported) | N/A | Medium | Investigate unusual noise reported by operations during rounds. | Found loose access-panel fastener; tightened; no mechanical fault found. | Site Engineering | Completed | 2026-09-24 | No further finding. | Illustrates a reactive work order outside the condition-monitoring pilot for comparison.

## Alert & Anomaly Register
Alert ID | Date/Time | Asset ID | Site ID | Monitoring Source | Failure Code | Severity | Alert Description | Engineering Review Outcome | Condition Validated | Status | Linked Work Order | Alert Classification (for KPI-T03/T04)
ALT-0001 | 2026-09-15 11:40 | IAD35-PUMP-01 | IAD35 | Vibration Sensor | V03 | High | Rising vibration amplitude at 1x running speed, trending above baseline over 5 days. | Engineering confirmed trend consistent with rotor imbalance signature. | Yes | Closed - Resolved | WO-1001 | True Positive
ALT-0002 | 2026-09-20 14:02 | ORD12-UPS-01 | ORD12 | Thermal Sensor | T01 | Critical | Localized hot spot at UPS input terminal, +22 degC delta-T vs. baseline. | Engineering escalated immediately given critical load path. | Yes | Closed - Resolved | WO-1002 | True Positive
ALT-0003 | 2026-09-27 03:18 | LHR10-LVSG-01 | LHR10 | Ultrasound Sensor | U02 | Critical | Ultrasonic acoustic signature consistent with early-stage arcing at breaker cable connection. | Engineering treated as urgent; redundant path confirmed available before action. | Yes | Closed - Resolved | WO-1003 | True Positive
ALT-0004 | 2026-10-02 09:05 | FRA15-XFMR-01 | FRA15 | Thermal Sensor | T04 | High | Gradual winding temperature rise beyond seasonal load-adjusted baseline. | Engineering requested oil sample and dissolved-gas analysis (DGA). | Pending Lab Result | Under Investigation | WO-1004 | Pending
ALT-0005 | 2026-10-05 16:44 | SIN11-GENS-01 | SIN11 | Vibration Sensor | V02 | Medium | Vibration signature consistent with minor coupling misalignment during weekly exercise run. | Engineering scheduled correction at next planned no-load run window. | Yes | Closed - Resolved | WO-1005 | True Positive
ALT-0006 | 2026-10-09 12:30 | SYD12-CHIL-01 | SYD12 | Vibration Sensor | V05 | Medium | Intermittent broadband vibration flagged as possible cavitation. | Physical inspection found no cavitation indicators; noise traced to an adjacent control valve. | No | Closed - False Positive | N/A | False Positive
ALT-0007 | 2026-10-14 08:12 | IAD35-CRAH-01 | IAD35 | Thermal Sensor | T05 | Medium | Fan motor casing temperature trending above baseline. | Engineering suspected belt slippage; scheduled inspection. | Yes | Closed - Resolved | WO-1006 | True Positive
ALT-0008 | 2026-10-18 19:55 | ORD12-PDU-01 | ORD12 | Ultrasound Sensor | U02 | Low | Low-level ultrasonic activity detected near PDU output breaker; below alarm threshold. | Queued for routine engineering review; not yet inspected. | Not Yet Reviewed | Open | N/A | Pending

## Condition Monitoring Readings
Reading ID | Date/Time | Asset ID | Sensor Type | Measured Value | Unit / Baseline | Threshold | Status | Linked Alert ID
RDG-0001 | 2026-09-08 09:15 | IAD35-PUMP-01 | Vibration | 2.1 | mm/s RMS | Alarm > 4.5 mm/s RMS | Normal | N/A
RDG-0002 | 2026-09-15 11:40 | IAD35-PUMP-01 | Vibration | 5.8 | mm/s RMS | Alarm > 4.5 mm/s RMS | Alarm | ALT-0001
RDG-0003 | 2026-09-18 15:00 | IAD35-PUMP-01 | Vibration | 2.4 | mm/s RMS | Alarm > 4.5 mm/s RMS | Normal (post-repair) | N/A
RDG-0004 | 2026-09-12 14:00 | ORD12-UPS-01 | Thermal | 46 | degC (baseline 44 degC) | Warning > +15 degC delta-T | Normal | N/A
RDG-0005 | 2026-09-20 14:02 | ORD12-UPS-01 | Thermal | 68 | degC (baseline 44 degC) | Warning > +15 degC delta-T | Alarm | ALT-0002
RDG-0006 | 2026-09-21 18:00 | ORD12-UPS-01 | Thermal | 45 | degC (post-repair) | Warning > +15 degC delta-T | Normal (post-repair) | N/A
RDG-0007 | 2026-09-27 03:18 | LHR10-LVSG-01 | Ultrasound | 41 | dB uV | Alarm > 38 dB uV | Alarm | ALT-0003
RDG-0008 | 2026-09-29 10:00 | LHR10-LVSG-01 | Ultrasound | 18 | dB uV (post-repair) | Alarm > 38 dB uV | Normal (post-repair) | N/A
RDG-0009 | 2026-10-02 09:05 | FRA15-XFMR-01 | Thermal | 79 | degC winding (baseline 61 degC) | Warning > +15 degC delta-T | Warning | ALT-0004
RDG-0010 | 2026-10-05 16:44 | SIN11-GENS-01 | Vibration | 3.9 | mm/s RMS | Warning > 3.5 mm/s RMS | Warning | ALT-0005
RDG-0011 | 2026-10-06 09:00 | SIN11-GENS-01 | Vibration | 1.8 | mm/s RMS (post-repair) | Warning > 3.5 mm/s RMS | Normal (post-repair) | N/A
RDG-0012 | 2026-10-09 12:30 | SYD12-CHIL-01 | Vibration | 3.6 | mm/s RMS | Warning > 3.5 mm/s RMS | Warning | ALT-0006
RDG-0013 | 2026-10-14 08:12 | IAD35-CRAH-01 | Thermal | 58 | degC motor casing (baseline 47 degC) | Warning > +10 degC delta-T | Warning | ALT-0007
RDG-0014 | 2026-10-18 19:55 | ORD12-PDU-01 | Ultrasound | 24 | dB uV | Alarm > 38 dB uV | Elevated (below alarm) | ALT-0008

## BMS Data Sample
Reading ID | Timestamp | Site ID | Location ID | Asset ID | BMS Point Name | Value | Unit | Status | Correlates With (Alert ID)
BMS-0001 | 2026-09-01 08:00 | IAD35 | IAD35-DHPOC | IAD35-CRAH-01 | Supply Air Temperature | 18.2 | degC | Normal | N/A
BMS-0002 | 2026-09-01 08:00 | IAD35 | IAD35-DHPOC | N/A (hall average) | Return Air Temperature | 24.5 | degC | Normal | N/A
BMS-0003 | 2026-09-01 08:00 | IAD35 | IAD35-DHPOC | N/A (hall average) | Relative Humidity | 45 | %RH | Normal | N/A
BMS-0004 | 2026-09-05 09:00 | ORD12 | ORD12-DHPOC | N/A (hall average) | Return Air Temperature | 23.9 | degC | Normal | N/A
BMS-0005 | 2026-09-10 10:00 | LHR10 | LHR10-DHPOC | N/A (hall average) | Chilled Water Valve Position | 62 | %Open | Normal | N/A
BMS-0006 | 2026-09-15 11:00 | FRA15 | FRA15-DHPOC | N/A (hall average) | Return Air Temperature | 24.1 | degC | Normal | N/A
BMS-0007 | 2026-09-20 12:00 | SIN11 | SIN11-DHPOC | N/A (hall average) | Relative Humidity | 48 | %RH | Normal | N/A
BMS-0008 | 2026-09-25 13:00 | SYD12 | SYD12-DHPOC | SYD12-CRAH-01 | Supply Air Temperature | 18.0 | degC | Normal | N/A
BMS-0009 | 2026-10-14 08:00 | IAD35 | IAD35-DHPOC | IAD35-CRAH-01 | Supply Air Temperature | 19.8 | degC | Warning - elevated | ALT-0007
BMS-0010 | 2026-10-14 08:05 | IAD35 | IAD35-DHPOC | IAD35-CRAH-01 | Fan Motor Damper Position | 88 | %Open (compensating) | Warning | ALT-0007
BMS-0011 | 2026-10-18 07:00 | IAD35 | IAD35-DHPOC | IAD35-CRAH-01 | Supply Air Temperature | 18.3 | degC (post-repair) | Normal (post-repair) | N/A
BMS-0012 | 2026-11-01 09:00 | ORD12 | ORD12-DHPOC | N/A (hall average) | Return Air Temperature | 23.7 | degC | Normal | N/A

## EPMS Data Sample
Reading ID | Timestamp | Site ID | Asset ID | EPMS Point Name | Value | Unit | Status | Correlates With (Alert ID)
EPMS-0001 | 2026-09-01 00:00 | LHR10 | LHR10-LVSG-01 | Bus Voltage L-L | 415 | V | Normal | N/A
EPMS-0002 | 2026-09-27 03:14 | LHR10 | LHR10-LVSG-01 | Harmonic Distortion (THD) | 4.8 | %THD | Warning | ALT-0003
EPMS-0003 | 2026-09-27 03:15 | LHR10 | LHR10-LVSG-01 | Ground Fault Current (Pre-Alarm) | 2.4 | A | Warning - precedes alert by 3 min | ALT-0003
EPMS-0004 | 2026-09-27 03:20 | LHR10 | LHR10-LVSG-01 | Breaker Status | Closed - No Trip | - | Normal (redundant path held) | ALT-0003
EPMS-0005 | 2026-09-05 06:00 | FRA15 | FRA15-XFMR-01 | Load | 68 | %Rated | Normal | N/A
EPMS-0006 | 2026-10-02 09:00 | FRA15 | FRA15-XFMR-01 | Load | 74 | %Rated | Normal (context for thermal alert) | ALT-0004
EPMS-0007 | 2026-09-10 07:00 | ORD12 | ORD12-UPS-01 | Output Current | 820 | A | Normal | N/A
EPMS-0008 | 2026-09-20 14:00 | ORD12 | ORD12-UPS-01 | Input Terminal Voltage Imbalance | 3.1 | % | Warning | ALT-0002
EPMS-0009 | 2026-09-21 18:00 | ORD12 | ORD12-UPS-01 | Input Terminal Voltage Imbalance | 0.4 | % (post-repair) | Normal (post-repair) | N/A
EPMS-0010 | 2026-09-12 08:00 | ORD12 | ORD12-PDU-01 | Branch Circuit Load | 58 | %Rated | Normal | N/A
EPMS-0011 | 2026-09-15 10:00 | IAD35 | IAD35-CHIL-01 | Motor Current | 210 | A | Normal | N/A
EPMS-0012 | 2026-09-20 11:00 | SIN11 | SIN11-HVSG-01 | Bus Voltage | 11 | kV | Normal | N/A
EPMS-0013 | 2026-09-25 12:00 | SYD12 | SYD12-GENS-01 | Standby Generator Output | 0 | kW (standby) | Normal | N/A
EPMS-0014 | 2026-11-01 09:00 | FRA15 | FRA15-LVSG-01 | Bus Voltage L-L | 400 | V | Normal | N/A

## DCIM Data Sample
Reading ID | Date | Site ID | Metric | Value | Unit | Trend Note
DCIM-0001 | 2026-09-01 | IAD35 | PUE (trailing 30-day) | 1.42 | ratio | Stable
DCIM-0002 | 2026-09-01 | IAD35 | Power Capacity Headroom | 22 | % of design | Adequate for N+1
DCIM-0003 | 2026-09-01 | ORD12 | PUE (trailing 30-day) | 1.48 | ratio | Stable
DCIM-0004 | 2026-09-01 | ORD12 | Cooling Capacity Headroom | 18 | % of design | Adequate for N+1
DCIM-0005 | 2026-09-01 | LHR10 | PUE (trailing 30-day) | 1.35 | ratio | Stable (2N site)
DCIM-0006 | 2026-09-01 | LHR10 | Power Capacity Headroom | 45 | % of design | Adequate for 2N
DCIM-0007 | 2026-09-01 | FRA15 | PUE (trailing 30-day) | 1.31 | ratio | Stable (2N site)
DCIM-0008 | 2026-09-01 | FRA15 | Power Capacity Headroom | 41 | % of design | Adequate for 2N
DCIM-0009 | 2026-09-01 | SIN11 | PUE (trailing 30-day) | 1.52 | ratio | Stable (tropical climate)
DCIM-0010 | 2026-09-01 | SIN11 | Cooling Capacity Headroom | 15 | % of design | Watch - trending down
DCIM-0011 | 2026-09-01 | SYD12 | PUE (trailing 30-day) | 1.39 | ratio | Stable
DCIM-0012 | 2026-11-01 | IAD35 | PUE (trailing 30-day) | 1.40 | ratio | Improved vs. September baseline

## OEM Monitoring Sample
Reading ID | Timestamp | Site ID | Asset ID | OEM Platform | Health Indicator / Alarm | Value / Description | Status | Correlates With (Alert ID)
OEM-0001 | 2026-09-10 07:00 | ORD12 | ORD12-UPS-01 | Vertiv LIFE Services | Module Health Score | 90/100 | Normal | N/A
OEM-0002 | 2026-09-20 14:00 | ORD12 | ORD12-UPS-01 | Vertiv LIFE Services | Module Health Score | 92/100 | Normal | N/A
OEM-0003 | 2026-09-20 14:02 | ORD12 | ORD12-UPS-01 | Vertiv LIFE Services | Remote Diagnostic Alert | Input terminal thermal anomaly flagged | Warning | ALT-0002
OEM-0004 | 2026-10-01 09:00 | LHR10 | LHR10-UPS-01 | Vertiv LIFE Services | Battery String Health Score | 88/100 | Normal | N/A
OEM-0005 | 2026-10-05 16:44 | SIN11 | SIN11-GENS-01 | Cummins PowerCommand Cloud | Vibration Advisory | Minor coupling misalignment flagged | Warning | ALT-0005
OEM-0006 | 2026-10-06 09:00 | SIN11 | SIN11-GENS-01 | Cummins PowerCommand Cloud | Engine Health Score | 96/100 (post-repair) | Normal (post-repair) | N/A
OEM-0007 | 2026-10-30 07:00 | FRA15 | FRA15-GENS-01 | MTU / Rolls-Royce ONCall | Engine Health Score | 94/100 | Normal | N/A
OEM-0008 | 2026-09-15 10:00 | IAD35 | IAD35-CHIL-01 | Trane Intelligent Services | Refrigeration Circuit Health Score | 91/100 | Normal | N/A
OEM-0009 | 2026-11-01 08:00 | SYD12 | SYD12-GENS-01 | Caterpillar VisionLink | Fuel System Advisory | Routine filter change due | Info | N/A

## Battery Monitoring Sample
Reading ID | Timestamp | Site ID | Asset ID | String / Cell Reference | Cell Voltage (V) | Internal Resistance (mOhm) | Temperature (degC) | State of Health (%) | Status
BAT-0001 | 2026-09-10 07:00 | ORD12 | ORD12-UPS-01 | String 1 - Cell 08 | 2.24 | 0.98 | 23 | 97 | Normal
BAT-0002 | 2026-10-01 06:00 | LHR10 | LHR10-UPS-01 | String 1 - Cell 14 | 2.23 | 1.05 | 24 | 96 | Normal
BAT-0003 | 2026-10-01 06:00 | LHR10 | LHR10-UPS-01 | String 2 - Cell 22 | 2.18 | 1.42 | 25 | 89 | Watch - trending
BAT-0004 | 2026-10-15 09:00 | LHR10 | LHR10-UPS-01 | String 2 - Cell 22 | 2.15 | 1.55 | 25 | 86 | Warning - added to PM watch list
BAT-0005 | 2026-09-20 12:00 | SIN11 | SIN11-BAT-01 | Standby Battery Bank - String 1 | 2.20 | 1.10 | 27 | 94 | Normal
BAT-0006 | 2026-11-01 08:00 | SIN11 | SIN11-BAT-01 | Standby Battery Bank - String 2 | 2.19 | 1.15 | 27 | 93 | Normal
BAT-0007 | 2026-09-25 13:00 | SYD12 | SYD12-BAT-01 | Standby Battery Bank - String 1 | 2.22 | 1.02 | 22 | 95 | Normal
BAT-0008 | 2026-11-15 06:00 | ORD12 | ORD12-UPS-01 | String 1 - Cell 08 | 2.23 | 1.01 | 23 | 96 | Normal

## Maintenance Correlation Log
Correlation ID | Linked Alert ID | Asset ID | Physical Inspection Date | Inspection/Maintenance Finding | Finding Confirmed Anomaly? | Failure Mode Confirmed | Detection Lead Time vs. Traditional PM | Maintenance Optimization Insight
COR-001 | ALT-0001 | IAD35-PUMP-01 | 2026-09-17 | Impeller wear consistent with the V03 imbalance vibration signature. | Yes | V03 - Imbalance | 18 days ahead of the next scheduled quarterly pump PM | Consider a condition-triggered PM interval for high-duty condenser water pumps.
COR-002 | ALT-0002 | ORD12-UPS-01 | 2026-09-20 | Loose input terminal lug confirmed as heat source. | Yes | T01 - Loose Electrical Connection | Detected before visible insulation damage or trip event | Add a thermal-scan checkpoint to the UPS quarterly PM checklist (PM-UPS-01).
COR-003 | ALT-0003 | LHR10-LVSG-01 | 2026-09-28 | Early-stage arcing confirmed at breaker cable lug; contact resurfaced. | Yes | U02 - Arcing | Approx. 9 months ahead of next annual IR thermography scan (PM-LVSG-01) | Ultrasound shows earlier lead time than annual IR scanning for LV switchgear connections.
COR-004 | ALT-0004 | FRA15-XFMR-01 | Pending | Pending dissolved-gas analysis (DGA) lab result. | Pending | T04 - Insulation Degradation (suspected) | TBD | To be updated once DGA result is received.
COR-005 | ALT-0005 | SIN11-GENS-01 | 2026-10-06 | Minor coupling misalignment confirmed and corrected during routine exercise run. | Yes | V02 - Misalignment | Corrected proactively; no unplanned outage risk incurred | Condition data actioned inside existing PM windows at no added operational risk.
COR-006 | ALT-0006 | SYD12-CHIL-01 | 2026-10-10 | No cavitation found; noise traced to an adjacent control valve, not the chiller. | No | N/A - False Positive | N/A | Refine vibration sensor placement/threshold near high-flow valves to reduce false positives.
COR-007 | ALT-0007 | IAD35-CRAH-01 | 2026-10-14 | Fan drive belt slippage confirmed and adjusted. | Yes | T05 - Motor Overheating (secondary cause: belt slippage) | Detected within normal monthly filter/belt PM window | Minor finding; no PM interval change recommended for this asset class.

## KPI Dashboard (Actuals)
KPI ID | Group | KPI | Target (SOW Sec. 8) | Actual (Live Formula) | Status vs. Target | Computed From
KPI-T01 | Technical | Sensor Availability | ~90-100% | 94.5% | On Target | Weekly Health Report Log - Sensor Availability %
KPI-T02 | Technical | Data Acquisition Reliability | ~90-100% | 95.62% | On Target | Weekly Health Report Log - Data Acquisition Reliability %
KPI-T03 | Technical | Alert Accuracy | ~70-80% | 83.33% | Above Target (favorable) | Alert & Anomaly Register - Alert Classification
KPI-T04 | Technical | False Positive Rate | ~10-20% | 16.67% | On Target | Alert & Anomaly Register - Alert Classification
KPI-T05 | Technical | Dashboard Availability | ~90-100% | 97.38% | On Target | Weekly Health Report Log - Dashboard Availability %
KPI-O01 | Operational | Early Fault Detection | Demonstrated | 5 | Demonstrated | Maintenance Correlation Log - Finding Confirmed Anomaly?
KPI-O02 | Operational | Reduced Unplanned Maintenance Risk | Demonstrated | 3 | Demonstrated | Alert & Anomaly Register - Critical/High True Positives
KPI-O03 | Operational | Maintenance Optimization Opportunities | Demonstrated | 7 | Demonstrated | Maintenance Correlation Log - review count (see Insight column for detail)
KPI-O04 | Operational | Condition-Based Interventions | Demonstrated | 5 | Demonstrated | Work Orders - Trigger Source = Condition-Based Alert, Status = Completed
KPI-O05 | Operational | Business Case for Scale | Developed | 6 | Developed | Benefits Realization Assessment - quantified benefit count

## Benefits Realization Assessment
Benefit ID | Category | Description | Linked Evidence | Estimated Impact (Illustrative) | Basis / Assumption
BEN-001 | Reliability | Early detection of switchgear arcing avoided a potential unplanned breaker trip on a Critical-rated LV switchgear asset. | COR-003 / WO-1003 | Avoided potential outage on a Critical asset; $ impact to be quantified with Digital Realty's outage-cost model. | Illustrative - requires Digital Realty incident-cost benchmark
BEN-002 | Reliability | Loose UPS input connection corrected before insulation failure on a Critical load path. | COR-002 / WO-1002 | Avoided potential critical-load risk event. | Illustrative - requires Digital Realty incident-cost benchmark
BEN-003 | Maintenance Efficiency | Vibration-based detection of pump imbalance found 18 days ahead of the next scheduled quarterly PM. | COR-001 / WO-1001 | 18-day earlier intervention than calendar-based PM would have provided. | Basis: PM Task Library task PM-PUMP-01 (Quarterly)
BEN-004 | Maintenance Efficiency | Generator coupling misalignment corrected inside an existing PM window at no incremental cost. | COR-005 / WO-1005 | Zero incremental maintenance window required. | Basis: existing PM-GENS-01 weekly no-load exercise run
BEN-005 | Analytics Quality | False-positive alert root-caused and used to refine vibration sensor placement/threshold. | COR-006 | Expected improvement in future Alert Accuracy (KPI-T03) and False Positive Rate (KPI-T04). | Feeds ongoing KPI-T03/T04 trend
BEN-006 | Business Case | 3 of 8 sample alerts (37.5%) were Critical-severity true positives on assets with no built-in redundancy margin (switchgear, UPS, transformer) - the segment most likely to justify global scale-up. | ALT-0002, ALT-0003, ALT-0004 | Indicative only; to be validated against the full 12-month PoC dataset. | Feeds Section 12 Go/No-Go recommendation

## PM Compliance Log
Log ID | PM Task ID (ref. Master Data) | Asset ID | Scheduled Date | Completed Date | Compliance Status | Assigned Team
PMC-001 | PM-CRAH-01 | IAD35-CRAH-01 | 2026-09-01 | 2026-09-01 | Completed On Time | Site Engineering
PMC-002 | PM-CHIL-01 | IAD35-CHIL-01 | 2026-09-15 | 2026-09-18 | Completed Late | Chiller OEM Vendor
PMC-003 | PM-UPS-01 | ORD12-UPS-01 | 2026-09-10 | 2026-09-10 | Completed On Time | Site Engineering
PMC-004 | PM-UPS-02 | LHR10-UPS-01 | 2026-10-01 | 2026-10-01 | Completed On Time | Site Engineering + Battery Vendor
PMC-005 | PM-LVSG-01 | LHR10-LVSG-01 | 2026-11-15 |  | Scheduled | Switchgear OEM
PMC-006 | PM-XFMR-01 | FRA15-XFMR-01 | 2026-10-20 |  | Scheduled (Advanced due to ALT-0004) | Site Engineering
PMC-007 | PM-GENS-01 | SIN11-GENS-01 | 2026-10-06 | 2026-10-06 | Completed On Time | Site Engineering
PMC-008 | PM-GENS-02 | SYD12-GENS-01 | 2026-11-01 |  | Scheduled | Generator OEM
PMC-009 | PM-CRAH-02 | SYD12-CRAH-01 | 2026-09-30 | 2026-10-05 | Completed Late | Site Engineering
PMC-010 | PM-PDU-01 | ORD12-PDU-01 | 2026-12-01 |  | Scheduled | Site Engineering

## Weekly Health Report Log
Report ID | Week Ending | Reporting Cadence | Sensor Availability % | Data Acquisition Reliability % | Dashboard Availability % | Open Alerts | Alerts Closed | Work Orders Raised | Key Observations | Prepared By
WHR-01 | 2026-09-05 | Weekly | 88% | 91% | 95% | 0 | 0 | 0 | Sensor commissioning in progress across all 6 sites; baselining under way. | Vendor PoC Lead
WHR-02 | 2026-09-12 | Weekly | 93% | 95% | 97% | 0 | 0 | 0 | All sites reporting baseline data; no alerts yet generated. | Vendor PoC Lead
WHR-03 | 2026-09-19 | Weekly | 95% | 96% | 98% | 2 | 1 | 2 | First two condition-based alerts (ALT-0001, ALT-0002) validated and actioned. | Vendor PoC Lead
WHR-04 | 2026-09-26 | Weekly | 96% | 97% | 99% | 1 | 2 | 1 | ALT-0003 (LV switchgear arcing) closed same week given criticality. | Vendor PoC Lead
WHR-05 | 2026-10-03 | Weekly | 94% | 95% | 96% | 2 | 1 | 2 | Transformer DGA sample pending lab turnaround; generator alert closed. | Vendor PoC Lead
WHR-06 | 2026-10-10 | Weekly | 97% | 97% | 98% | 1 | 1 | 1 | First false-positive alert identified and root-caused (ALT-0006); threshold review opened. | Vendor PoC Lead
WHR-07 | 2026-10-24 | Biweekly (transition per SOW 2.1) | 96% | 96% | 97% | 1 | 1 | 1 | Moved to biweekly cadence as PoC stabilizes; CRAH belt finding closed. | Vendor PoC Lead
WHR-08 | 2026-11-07 | Biweekly | 97% | 98% | 99% | 1 | 0 | 0 | Stable operation; PDU ultrasound alert queued for routine review. | Vendor PoC Lead

## Incident History (Baseline)
Incident ID | Date | Asset ID | Site ID | Failure Description | Root Cause | Detection Method (Traditional) | Downtime (hrs) | Customer-Facing Impact
INC-2025-014 | 2025-03-11 | ORD12-UPS-01 | ORD12 | UPS module fault on redundant leg; load remained on active module. | Capacitor failure (age-related). | BMS Alarm | 0 (redundant) | No
INC-2025-027 | 2025-06-22 | LHR10-LVSG-01 | LHR10 | Nuisance trip on non-critical distribution breaker. | Protective relay settings drift. | EPMS Alarm | 1.5 | No
INC-2025-041 | 2025-08-04 | IAD35-CHIL-01 | IAD35 | Reduced chiller capacity during peak cooling demand. | Fouled condenser tubes. | Operator Report + BMS Trend | 0 (N+1 covered) | No
INC-2025-058 | 2025-10-30 | FRA15-GENS-01 | FRA15 | Failed to reach rated load during scheduled load-bank test. | Fuel filter restriction. | Scheduled PM (PM-GENS-02) | N/A (test) | No
INC-2026-009 | 2026-02-14 | SIN11-XFMR-01 | SIN11 | Elevated top-oil temperature alarm during high-load period. | Cooling fan controller fault. | BMS Alarm | 0 (corrected same shift) | No
INC-2026-021 | 2026-05-02 | SYD12-CHIL-01 | SYD12 | Unplanned chiller trip on high discharge pressure. | Condenser water flow restriction. | BMS Alarm | 0.5 (N+1 covered) | No
INC-2026-033 | 2026-06-19 | ORD12-PDU-01 | ORD12 | Breaker overheating identified during routine inspection. | Loose termination. | Scheduled PM Inspection | 0 | No

## Risk-Assumption-Dependency Reg
ID | Category | Description | Likelihood | Impact | Mitigation / Response | Owner | Status
RSK-001 | Risk | Limited historical data on asset condition prior to PoC. | Medium | Medium | Establish baseline operating profiles during initial commissioning weeks. | Vendor PoC Lead | Open
RSK-002 | Risk | Live site access restrictions limit installation windows. | Medium | Medium | Coordinate sensor installation during approved maintenance windows. | Site Leadership | Open
RSK-003 | Risk | Sensor communication issues (wireless interference, gateway outage). | Medium | Low | Use redundant collection methods and offline data buffering. | Vendor PoC Lead | Open
RSK-004 | Risk | Change resistance from site operations teams. | Low | Medium | Stakeholder engagement, training, and clear MOP alignment. | Regional Operations | Open
RSK-005 | Risk | Data quality issues (sensor drift, calibration gaps). | Medium | Medium | Data validation, cleansing, and periodic calibration checks. | Vendor PoC Lead | Open
RSK-006 | Risk | Environmental noise impacts sensor accuracy (electrical/mechanical background noise). | Medium | Low | Multi-sensor correlation validation before alert escalation. | Vendor PoC Lead | Open
ASM-001 | Assumption | Digital Realty will provide network/VLAN and firewall access within agreed STEP timelines. | N/A | High if delayed | Confirmed in Technical Prereq Checklist prior to installation. | Digital Realty IT/OT | Open
ASM-002 | Assumption | Existing BMS/EPMS/DCIM systems expose the data points required without custom development. | N/A | High if false | Validate integration points during Detailed Technical Solution Design (SOW 5.1). | Vendor PoC Lead | Open
DEP-001 | Dependency | Final Asset Scope Matrix approval by Digital Realty before installation begins (SOW 3.3). | N/A | Blocks installation | Submit within 10 business days of project initiation; track approval status. | Digital Realty Reliability Engineering | Pending Approval
DEP-002 | Dependency | Site Leadership approval of maintenance/change windows for non-intrusive installation. | N/A | Blocks installation | Coordinate schedule via Site Readiness Checklist. | Site Leadership | Pending Approval

## Site Readiness Checklist
SOW 5.2 Category | Checklist Item | Applies To | Status | Owner
Site prerequisites & readiness | Confirm selected PoC data hall/zone and physical access route | All 6 Sites | Not Started | Site Leadership
Site prerequisites & readiness | Confirm site safety induction/orientation completed for vendor personnel | All 6 Sites | Not Started | Site Leadership
System access & permissions | Provision read-only BMS/EPMS/DCIM accounts for vendor analytics platform | All 6 Sites | Not Started | Digital Realty IT/OT
Data sources & availability | Confirm 12 months of CMMS maintenance history exportable for baseline | All 6 Sites | Not Started | Asset Management
Asset information & documentation | Provide as-built drawings and OEM manuals for in-scope assets | All 6 Sites | Not Started | Site Engineering
Infrastructure & network | Confirm available network drops / wireless coverage in PoC zone | All 6 Sites | Not Started | Digital Realty IT/OT
Connectivity & integration | Validate BMS/EPMS/DCIM API or gateway integration endpoints | All 6 Sites | Not Started | Vendor PoC Lead
Cybersecurity & compliance | Complete cybersecurity review of sensor/gateway data pathway | All 6 Sites | Not Started | Digital Realty IT/OT
Hardware / software / licensing | Confirm sensor hardware and analytics platform licenses procured | All 6 Sites | Not Started | Vendor PoC Lead
Environmental & installation | Confirm mounting locations meet OEM environmental specifications | All 6 Sites | Not Started | Site Engineering
Site access & scheduling | Agree installation schedule and escort requirements per site | All 6 Sites | Not Started | Site Leadership
Change management / maintenance windows | Approve Method of Procedure (MOP) for non-intrusive installation | All 6 Sites | Not Started | Site Leadership
Digital Realty resources & stakeholders | Confirm named Site Engineering and Reliability Engineering contacts | All 6 Sites | Not Started | Regional Operations
Vendor dependencies & assumptions | Confirm vendor technology partner (sensor OEM) selected and available | All 6 Sites | Not Started | Vendor PoC Lead
Required approvals | Final Asset Scope Matrix and Solution Design Package approved (SOW 5.1/3.3) | All 6 Sites | Not Started | Digital Realty Reliability Engineering

## Technical Prereq Checklist
Category | Checklist Item | Status | Owner
Network | VLAN / subnet allocated for sensor gateways | Not Started | Digital Realty IT/OT
Network | Firewall rules approved for gateway-to-cloud analytics traffic | Not Started | Digital Realty IT/OT
Cybersecurity | Sensor/gateway firmware security review completed | Not Started | Digital Realty IT/OT
Cybersecurity | Data-in-transit and data-at-rest encryption confirmed | Not Started | Vendor PoC Lead
Power | Local power source identified for sensor gateways (non-critical circuit) | Not Started | Site Engineering
Mounting / Installation | Mounting locations identified and approved (non-intrusive, no shutdown) | Not Started | Site Engineering
Integration | BMS/EPMS/DCIM data-point mapping confirmed against Section 4.1 sources | Not Started | Vendor PoC Lead
Integration | CMMS maintenance-history export format confirmed | Not Started | Asset Management
Software / Licensing | Analytics dashboard licenses provisioned for named users | Not Started | Vendor PoC Lead
Access | Vendor personnel badge access and escort requirements confirmed | Not Started | Site Leadership
Change Management | MOP submitted and approved for installation/commissioning activities | Not Started | Site Leadership
Training | Operations team training session scheduled (SOW 5.4) | Not Started | Regional Operations