Future State Maintenance (FSM) PoC

Consolidated reference — Analytics & Monitoring

Client: Digital Realty  ·  Site scope: EMEA, NAM, APAC  ·  Prepared for: Development team

This document consolidates everything covered on the Analytics & Monitoring workstream of the FSM PoC: the objectives explained in plain terms, the detection-to-feedback data flow, a full end-to-end example on a real asset, the demo screen specifications, and a summary of the synthetic asset data prepared for the team.

Companion files (referenced but not duplicated in full here): FSM_PoC_Demo_Screens_Spec.pdf (detailed screen build spec) and FSM_PoC_Synthetic_Asset_Data.xlsx (underlying demo data).

# 1. Objectives 2–6, explained for the dev team

Goal in one line: hook up sensors and old data systems, catch equipment problems early, and prove it saves money. Below is what each objective means in practice and what we build for it.

## Objective 2 — Integrate existing telemetry with new sensors

What it means: Pull data from BMS, EPMS, DCIM, OEM platforms, and CMMS together with new vibration, thermal, and ultrasound sensors into one place, in one format.

What we build:

- Connectors/APIs to pull data out of BMS, EPMS, DCIM, CMMS, OEM systems.

- Gateways to bring in vibration, thermal, and ultrasound sensor data.

- A normalization layer — everything gets time-synced and converted into one common schema.

- One dashboard where all of this shows up together.

## Objective 3 — Catch problems earlier than current maintenance does

What it means: Catch mechanical, electrical, and thermal problems from the data before they'd be caught on a routine calendar-based inspection.

What we build:

- Threshold + trend detection per asset (e.g. rising vibration amplitude over 2 weeks = bearing wear starting).

- Logic per failure mode: bearing wear, misalignment, imbalance (vibration); loose connections, overheating, insulation breakdown (thermal); arcing, corona discharge, lubrication breakdown (ultrasound).

- Alerting that fires before the next scheduled inspection would have caught it.

## Objective 4 — Turn a detected problem into a clear maintenance action

What it means: An alert alone isn't useful — it needs to tell the engineer what to do about it.

What we build:

- A recommendation engine mapping detected condition → suggested action (e.g. "vibration signature matches bearing wear on Pump 3 → schedule bearing inspection within 2 weeks").

- Each recommendation includes: asset, likely issue, urgency, next step.

- Connects into the response workflow: alert → engineering review → condition validation → maintenance action → work order.

## Objective 5 — Check alerts against what technicians actually find

What it means: When a technician inspects an asset after an alert, record whether the system was right. This is how we prove and tune the system.

What we build:

- A correlation log: alert ID → work order → inspection outcome (confirmed / false positive / different issue).

- A way for technicians to log findings back into the system.

- Reporting on alert accuracy and false positive rate over time (maps to SOW KPIs: Alert Accuracy ~70–80%, False Positive Rate ~10–20%).

## Objective 6 — Prove the business value

What it means: By the end of the PoC, show numbers: failures caught early, downtime/cost avoided, and where maintenance could be optimized.

What we build:

- Tracking for early detections, estimated avoided failures, and condition-based vs. calendar-based maintenance actions.

- A simple ROI/benefits calculation, even rough estimates.

- A stakeholder summary view feeding the Final PoC report and Benefits Realization Assessment.

# 2. Data flow — sensors to analytics to action

The pipeline every screen and every objective above sits on top of:

- Sensors (vibration / thermal / ultrasound) + existing systems (BMS/EPMS/DCIM/CMMS)

- → Data ingestion (time-synced, normalized into one schema)

- → Analytics engine (thresholds, trends, health scoring, cross-sensor correlation)

- → Outputs: alerts & dashboard, asset health score, maintenance recommendations

- → Field verification (technician inspects, logs outcome)

- → feeds back into the analytics engine — this loop is what proves and improves accuracy

See the flow diagrams shared earlier in this chat for the visual versions of this pipeline, including the standalone cross-sensor correlation step.

## Why cross-sensor correlation matters

A single sensor crossing a threshold is a weak signal on its own. Before a failure code is confirmed, the other two sensor types are checked against the same asset over the same time window:

- Vibration rising + thermal stable + ultrasound stable → treated as a lower-confidence signal.

- Vibration rising + thermal rising + ultrasound rising (agreement) → confidence increases, e.g. 82% → 91%.

- This is what should visibly change in the UI — a label like "confirmed by 2 of 3 sensors" — since it's the detail that proves the multi-sensor approach earns its keep over single-sensor monitoring.

# 3. End-to-end example — CRAH-01 bearing wear

This is the story used to walk the client through the full workflow on one real asset.

## 3.1 Detection phase

| Step | What happens |
| --- | --- |
| Continuous monitoring | Vibration, thermal, and ultrasound sensors stream data continuously. |
| Anomaly detected | Vibration trends above baseline for 16 days. |
| Cross-sensor correlation | Thermal and ultrasound readings checked against the same window — both confirm. |
| Failure code confirmed | VIB-BRG-04 (bearing wear); confidence rises from 82% to 91% with corroboration. |
| Health score updated | Score drops from 92 to 68. |

## 3.2 Response and feedback phase

| Step | What happens |
| --- | --- |
| Alert generated | Pushed to the dashboard and stakeholder feed. |
| Engineering review | Engineer validates the alert against trend data. |
| Recommendation issued | "Inspect bearing within 2 weeks." |
| Work order and inspection | Technician inspects, logs finding in CMMS. |
| Outcome logged | Confirmed true positive — feeds back to tune thresholds. |

# 4. Recommended demo screens

Six screens cover the full workflow above, built on one shared data model so moving between them is a filter change, not a different system. (Full field-level spec is in the companion PDF — this is the summary.)

| Screen | Purpose |
| --- | --- |
| Asset overview / fleet view | Every monitored asset at a glance: health score, status, last alert. The landing screen for the demo. |
| Asset detail / live monitoring | The deep-dive screen for one asset: sensor readouts, health score, active alert, recommendation. Where the demo spends the most time. |
| Trend analysis | Time-series chart per sensor proving early detection, with the alert point marked against the threshold crossing. |
| Alert & failure code detail | What was detected, which sensors agreed, confidence score, severity, status. |
| Maintenance recommendation / work order | The alert turning into an actual action: recommendation, urgency, work order status, technician finding, outcome. |
| Correlation / outcome log | The accuracy proof screen — predicted vs. actual findings, rolling accuracy and false-positive rate against KPI targets. |

## KPI reference

| KPI | Target |
| --- | --- |
| Sensor availability | ~90–100% |
| Data acquisition reliability | ~90–100% |
| Alert accuracy | ~70–80% |
| False positive rate | ~10–20% |
| Dashboard availability | ~90–100% |

# 5. Synthetic demo data

30 days of synthetic sensor and workflow data was generated for three real assets, each demonstrating a different point in the workflow so the demo shows range, not just one success story. Full data lives in FSM_PoC_Synthetic_Asset_Data.xlsx (sheets: Assets, Sensor_Readings, Health_Score_History, Alerts, Recommendations_WorkOrders).

| Asset | Scenario | Demo state |
| --- | --- | --- |
| IAD35-CRAH-01 — CRAH Unit 01 | Bearing wear: vibration, thermal, and ultrasound all trend up together over the window. | Alert raised, work order completed, outcome confirmed true positive — the full closed loop. |
| IAD35-CRAC-01 — CRAC Unit 01 | Electrical fault: thermal and ultrasound spike sharply in the final ~10 days; vibration stays flat. | Alert active, under engineering review, work order dispatched but not yet closed — a mid-workflow state. |
| IAD35-CHIL-01 — Chiller 01 | Healthy baseline: all three sensors flat with normal noise, no trend. | No alerts — shows the system isn't crying wolf on a healthy asset. |