## Assets
Asset_ID | Asset_Name | Asset_Class | Site | Location | Criticality | Manufacturer | Monitoring_Methods | Install_Date | Current_Status
IAD35-CRAH-01 | CRAH Unit 01 | Mechanical - Cooling | IAD35 | Data Hall 3 | Critical | Vertiv | Vibration, Thermal, Ultrasound, BMS | 2019-06-12 | Alert - Critical
IAD35-CRAC-01 | CRAC Unit 01 | Mechanical - Cooling | IAD35 | Data Hall 1 | Critical | Liebert | Vibration, Thermal, Ultrasound, BMS | 2018-03-05 | Alert - Warning
IAD35-CHIL-01 | Chiller 01 | Mechanical - Cooling | IAD35 | Central Plant | Critical | Trane | Vibration, Thermal, Ultrasound, BMS, EPMS | 2020-11-20 | Healthy

## Sensor_Readings
Date | Asset_ID | Vibration_mms | Vibration_Status | Thermal_C | Thermal_Status | Ultrasound_dB | Ultrasound_Status
2026-07-22 | IAD35-CRAH-01 | 2.03 | Normal | 33.43 | Normal | 18.55 | Normal
2026-07-23 | IAD35-CRAH-01 | 1.93 | Normal | 34.28 | Normal | 19.35 | Normal
2026-07-24 | IAD35-CRAH-01 | 2.09 | Normal | 33.5 | Normal | 18.84 | Normal
2026-07-25 | IAD35-CRAH-01 | 1.89 | Normal | 33.66 | Normal | 19.01 | Normal
2026-07-26 | IAD35-CRAH-01 | 1.89 | Normal | 33.64 | Normal | 19.3 | Normal
2026-07-27 | IAD35-CRAH-01 | 2.01 | Normal | 33.66 | Normal | 19.18 | Normal
2026-07-28 | IAD35-CRAH-01 | 2.07 | Normal | 33.41 | Normal | 19.61 | Normal
2026-07-29 | IAD35-CRAH-01 | 2.05 | Normal | 33.81 | Normal | 18.31 | Normal
2026-07-30 | IAD35-CRAH-01 | 2.11 | Normal | 33.8 | Normal | 18.19 | Normal
2026-07-31 | IAD35-CRAH-01 | 2.04 | Normal | 34.82 | Normal | 20.02 | Normal
2026-08-01 | IAD35-CRAH-01 | 2.35 | Normal | 35.09 | Normal | 20.69 | Normal
2026-08-02 | IAD35-CRAH-01 | 2.53 | Normal | 35.07 | Normal | 21.53 | Normal
2026-08-03 | IAD35-CRAH-01 | 2.63 | Normal | 35.76 | Normal | 22.96 | Normal
2026-08-04 | IAD35-CRAH-01 | 2.71 | Normal | 36.27 | Normal | 22.14 | Normal
2026-08-05 | IAD35-CRAH-01 | 2.76 | Normal | 36.18 | Normal | 23.02 | Normal
2026-08-06 | IAD35-CRAH-01 | 2.9 | Normal | 36.35 | Normal | 24.22 | Normal
2026-08-07 | IAD35-CRAH-01 | 3.14 | Elevated | 37.08 | Normal | 25.22 | Normal
2026-08-08 | IAD35-CRAH-01 | 3.17 | Elevated | 37.36 | Normal | 27.16 | Normal
2026-08-09 | IAD35-CRAH-01 | 3.42 | Elevated | 38.18 | Elevated | 26.44 | Normal
2026-08-10 | IAD35-CRAH-01 | 3.57 | Elevated | 38.05 | Elevated | 27.66 | Normal
2026-08-11 | IAD35-CRAH-01 | 3.77 | Elevated | 39.03 | Elevated | 28.83 | Elevated
2026-08-12 | IAD35-CRAH-01 | 3.84 | Elevated | 39.67 | Elevated | 30.08 | Elevated
2026-08-13 | IAD35-CRAH-01 | 3.87 | Elevated | 39.11 | Elevated | 29.96 | Elevated
2026-08-14 | IAD35-CRAH-01 | 4.02 | Elevated | 39.72 | Elevated | 32.03 | Elevated
2026-08-15 | IAD35-CRAH-01 | 4.3 | Elevated | 40.25 | Elevated | 32.26 | Elevated
2026-08-16 | IAD35-CRAH-01 | 4.32 | Elevated | 41.38 | Above threshold | 32.68 | Elevated
2026-08-17 | IAD35-CRAH-01 | 4.43 | Elevated | 40.98 | Elevated | 33.69 | Elevated
2026-08-18 | IAD35-CRAH-01 | 4.57 | Above threshold | 41.79 | Above threshold | 35.18 | Above threshold
2026-08-19 | IAD35-CRAH-01 | 4.74 | Above threshold | 41.76 | Above threshold | 36.19 | Above threshold
2026-08-20 | IAD35-CRAH-01 | 4.9 | Above threshold | 42.01 | Above threshold | 35.09 | Above threshold
2026-07-22 | IAD35-CRAC-01 | 1.38 | Normal | 29.18 | Normal | 14.7 | Normal
2026-07-23 | IAD35-CRAC-01 | 1.48 | Normal | 28.39 | Normal | 13.72 | Normal
2026-07-24 | IAD35-CRAC-01 | 1.65 | Normal | 29.04 | Normal | 15.13 | Normal
2026-07-25 | IAD35-CRAC-01 | 1.61 | Normal | 28.32 | Normal | 14.53 | Normal
2026-07-26 | IAD35-CRAC-01 | 1.55 | Normal | 29.05 | Normal | 13.44 | Normal
2026-07-27 | IAD35-CRAC-01 | 1.54 | Normal | 28.46 | Normal | 13.84 | Normal
2026-07-28 | IAD35-CRAC-01 | 1.49 | Normal | 29.64 | Normal | 14.9 | Normal
2026-07-29 | IAD35-CRAC-01 | 1.43 | Normal | 29 | Normal | 13.23 | Normal
2026-07-30 | IAD35-CRAC-01 | 1.62 | Normal | 29.52 | Normal | 13.52 | Normal
2026-07-31 | IAD35-CRAC-01 | 1.54 | Normal | 29.15 | Normal | 13.17 | Normal
2026-08-01 | IAD35-CRAC-01 | 1.58 | Normal | 29.06 | Normal | 14.67 | Normal
2026-08-02 | IAD35-CRAC-01 | 1.51 | Normal | 28.3 | Normal | 13.58 | Normal
2026-08-03 | IAD35-CRAC-01 | 1.36 | Normal | 29.6 | Normal | 14.91 | Normal
2026-08-04 | IAD35-CRAC-01 | 1.6 | Normal | 28.73 | Normal | 12.94 | Normal
2026-08-05 | IAD35-CRAC-01 | 1.61 | Normal | 29.63 | Normal | 13.01 | Normal
2026-08-06 | IAD35-CRAC-01 | 1.5 | Normal | 28.4 | Normal | 14.63 | Normal
2026-08-07 | IAD35-CRAC-01 | 1.58 | Normal | 28.48 | Normal | 13.94 | Normal
2026-08-08 | IAD35-CRAC-01 | 1.51 | Normal | 28.67 | Normal | 14.89 | Normal
2026-08-09 | IAD35-CRAC-01 | 1.48 | Normal | 28.6 | Normal | 14.09 | Normal
2026-08-10 | IAD35-CRAC-01 | 1.57 | Normal | 28.58 | Normal | 13.55 | Normal
2026-08-11 | IAD35-CRAC-01 | 1.65 | Normal | 29.21 | Normal | 13.85 | Normal
2026-08-12 | IAD35-CRAC-01 | 1.51 | Normal | 30.58 | Normal | 16.56 | Normal
2026-08-13 | IAD35-CRAC-01 | 1.45 | Normal | 33.35 | Normal | 19.8 | Normal
2026-08-14 | IAD35-CRAC-01 | 1.42 | Normal | 34.73 | Normal | 23.98 | Normal
2026-08-15 | IAD35-CRAC-01 | 1.42 | Normal | 38.01 | Elevated | 27.75 | Normal
2026-08-16 | IAD35-CRAC-01 | 1.37 | Normal | 39.19 | Elevated | 30.52 | Elevated
2026-08-17 | IAD35-CRAC-01 | 1.41 | Normal | 41.15 | Elevated | 34.38 | Elevated
2026-08-18 | IAD35-CRAC-01 | 1.52 | Normal | 43.74 | Elevated | 37.24 | Elevated
2026-08-19 | IAD35-CRAC-01 | 1.59 | Normal | 45.46 | Above threshold | 38.81 | Above threshold
2026-08-20 | IAD35-CRAC-01 | 1.48 | Normal | 47.89 | Above threshold | 42.92 | Above threshold
2026-07-22 | IAD35-CHIL-01 | 1.87 | Normal | 28.28 | Normal | 19.26 | Normal
2026-07-23 | IAD35-CHIL-01 | 1.68 | Normal | 27.84 | Normal | 17.58 | Normal
2026-07-24 | IAD35-CHIL-01 | 1.91 | Normal | 27.6 | Normal | 17.19 | Normal
2026-07-25 | IAD35-CHIL-01 | 1.78 | Normal | 27.88 | Normal | 17.42 | Normal
2026-07-26 | IAD35-CHIL-01 | 1.72 | Normal | 28.68 | Normal | 17.85 | Normal
2026-07-27 | IAD35-CHIL-01 | 1.91 | Normal | 28.08 | Normal | 16.83 | Normal
2026-07-28 | IAD35-CHIL-01 | 1.95 | Normal | 28.54 | Normal | 19.22 | Normal
2026-07-29 | IAD35-CHIL-01 | 1.93 | Normal | 28.56 | Normal | 17.13 | Normal
2026-07-30 | IAD35-CHIL-01 | 1.8 | Normal | 27.54 | Normal | 17.74 | Normal
2026-07-31 | IAD35-CHIL-01 | 1.67 | Normal | 27.81 | Normal | 19.26 | Normal
2026-08-01 | IAD35-CHIL-01 | 1.73 | Normal | 28.45 | Normal | 17.88 | Normal
2026-08-02 | IAD35-CHIL-01 | 1.78 | Normal | 28.73 | Normal | 19.29 | Normal
2026-08-03 | IAD35-CHIL-01 | 1.82 | Normal | 28.35 | Normal | 17.1 | Normal
2026-08-04 | IAD35-CHIL-01 | 1.74 | Normal | 28.75 | Normal | 18.21 | Normal
2026-08-05 | IAD35-CHIL-01 | 1.81 | Normal | 28.4 | Normal | 16.85 | Normal
2026-08-06 | IAD35-CHIL-01 | 1.83 | Normal | 28 | Normal | 18.92 | Normal
2026-08-07 | IAD35-CHIL-01 | 1.7 | Normal | 28.74 | Normal | 16.91 | Normal
2026-08-08 | IAD35-CHIL-01 | 1.71 | Normal | 28.15 | Normal | 18.46 | Normal
2026-08-09 | IAD35-CHIL-01 | 1.72 | Normal | 27.39 | Normal | 19.01 | Normal
2026-08-10 | IAD35-CHIL-01 | 1.72 | Normal | 28.15 | Normal | 18.31 | Normal
2026-08-11 | IAD35-CHIL-01 | 1.78 | Normal | 28.13 | Normal | 18.06 | Normal
2026-08-12 | IAD35-CHIL-01 | 1.93 | Normal | 27.53 | Normal | 18.56 | Normal
2026-08-13 | IAD35-CHIL-01 | 1.72 | Normal | 27.83 | Normal | 18.45 | Normal
2026-08-14 | IAD35-CHIL-01 | 1.74 | Normal | 27.71 | Normal | 18.65 | Normal
2026-08-15 | IAD35-CHIL-01 | 1.67 | Normal | 27.93 | Normal | 19.3 | Normal
2026-08-16 | IAD35-CHIL-01 | 1.95 | Normal | 27.32 | Normal | 17.25 | Normal
2026-08-17 | IAD35-CHIL-01 | 1.73 | Normal | 28.69 | Normal | 18.99 | Normal
2026-08-18 | IAD35-CHIL-01 | 1.91 | Normal | 27.79 | Normal | 17.11 | Normal
2026-08-19 | IAD35-CHIL-01 | 1.9 | Normal | 28.33 | Normal | 18.29 | Normal
2026-08-20 | IAD35-CHIL-01 | 1.95 | Normal | 28.25 | Normal | 16.72 | Normal

## Health_Score_History
Date | Asset_ID | Health_Score
2026-07-22 | IAD35-CRAH-01 | 92
2026-07-23 | IAD35-CRAH-01 | 92
2026-07-24 | IAD35-CRAH-01 | 92
2026-07-25 | IAD35-CRAH-01 | 92
2026-07-26 | IAD35-CRAH-01 | 92
2026-07-27 | IAD35-CRAH-01 | 92
2026-07-28 | IAD35-CRAH-01 | 92
2026-07-29 | IAD35-CRAH-01 | 92
2026-07-30 | IAD35-CRAH-01 | 92
2026-07-31 | IAD35-CRAH-01 | 91
2026-08-01 | IAD35-CRAH-01 | 90
2026-08-02 | IAD35-CRAH-01 | 89
2026-08-03 | IAD35-CRAH-01 | 87
2026-08-04 | IAD35-CRAH-01 | 86
2026-08-05 | IAD35-CRAH-01 | 85
2026-08-06 | IAD35-CRAH-01 | 84
2026-08-07 | IAD35-CRAH-01 | 83
2026-08-08 | IAD35-CRAH-01 | 82
2026-08-09 | IAD35-CRAH-01 | 81
2026-08-10 | IAD35-CRAH-01 | 79
2026-08-11 | IAD35-CRAH-01 | 78
2026-08-12 | IAD35-CRAH-01 | 77
2026-08-13 | IAD35-CRAH-01 | 76
2026-08-14 | IAD35-CRAH-01 | 75
2026-08-15 | IAD35-CRAH-01 | 74
2026-08-16 | IAD35-CRAH-01 | 73
2026-08-17 | IAD35-CRAH-01 | 71
2026-08-18 | IAD35-CRAH-01 | 70
2026-08-19 | IAD35-CRAH-01 | 69
2026-08-20 | IAD35-CRAH-01 | 68
2026-07-22 | IAD35-CRAC-01 | 90
2026-07-23 | IAD35-CRAC-01 | 90
2026-07-24 | IAD35-CRAC-01 | 90
2026-07-25 | IAD35-CRAC-01 | 90
2026-07-26 | IAD35-CRAC-01 | 90
2026-07-27 | IAD35-CRAC-01 | 90
2026-07-28 | IAD35-CRAC-01 | 90
2026-07-29 | IAD35-CRAC-01 | 90
2026-07-30 | IAD35-CRAC-01 | 90
2026-07-31 | IAD35-CRAC-01 | 90
2026-08-01 | IAD35-CRAC-01 | 90
2026-08-02 | IAD35-CRAC-01 | 90
2026-08-03 | IAD35-CRAC-01 | 90
2026-08-04 | IAD35-CRAC-01 | 90
2026-08-05 | IAD35-CRAC-01 | 90
2026-08-06 | IAD35-CRAC-01 | 90
2026-08-07 | IAD35-CRAC-01 | 90
2026-08-08 | IAD35-CRAC-01 | 90
2026-08-09 | IAD35-CRAC-01 | 90
2026-08-10 | IAD35-CRAC-01 | 90
2026-08-11 | IAD35-CRAC-01 | 90
2026-08-12 | IAD35-CRAC-01 | 88
2026-08-13 | IAD35-CRAC-01 | 86
2026-08-14 | IAD35-CRAC-01 | 85
2026-08-15 | IAD35-CRAC-01 | 83
2026-08-16 | IAD35-CRAC-01 | 81
2026-08-17 | IAD35-CRAC-01 | 79
2026-08-18 | IAD35-CRAC-01 | 78
2026-08-19 | IAD35-CRAC-01 | 76
2026-08-20 | IAD35-CRAC-01 | 74
2026-07-22 | IAD35-CHIL-01 | 97
2026-07-23 | IAD35-CHIL-01 | 95
2026-07-24 | IAD35-CHIL-01 | 96
2026-07-25 | IAD35-CHIL-01 | 97
2026-07-26 | IAD35-CHIL-01 | 95
2026-07-27 | IAD35-CHIL-01 | 95
2026-07-28 | IAD35-CHIL-01 | 95
2026-07-29 | IAD35-CHIL-01 | 96
2026-07-30 | IAD35-CHIL-01 | 95
2026-07-31 | IAD35-CHIL-01 | 96
2026-08-01 | IAD35-CHIL-01 | 97
2026-08-02 | IAD35-CHIL-01 | 95
2026-08-03 | IAD35-CHIL-01 | 96
2026-08-04 | IAD35-CHIL-01 | 95
2026-08-05 | IAD35-CHIL-01 | 96
2026-08-06 | IAD35-CHIL-01 | 97
2026-08-07 | IAD35-CHIL-01 | 97
2026-08-08 | IAD35-CHIL-01 | 95
2026-08-09 | IAD35-CHIL-01 | 96
2026-08-10 | IAD35-CHIL-01 | 95
2026-08-11 | IAD35-CHIL-01 | 95
2026-08-12 | IAD35-CHIL-01 | 97
2026-08-13 | IAD35-CHIL-01 | 96
2026-08-14 | IAD35-CHIL-01 | 95
2026-08-15 | IAD35-CHIL-01 | 97
2026-08-16 | IAD35-CHIL-01 | 96
2026-08-17 | IAD35-CHIL-01 | 96
2026-08-18 | IAD35-CHIL-01 | 95
2026-08-19 | IAD35-CHIL-01 | 95
2026-08-20 | IAD35-CHIL-01 | 97

## Alerts
Alert_ID | Asset_ID | Date_Raised | Failure_Code | Description | Triggering_Sensors | Confidence_Pct | Severity | Status
ALT-1001 | IAD35-CRAH-01 | 2026-08-15 | VIB-BRG-04 | Bearing wear suspected; vibration trend confirmed by thermal and ultrasound signatures. | Vibration, Thermal, Ultrasound | 91% | Critical | Work order dispatched
ALT-1002 | IAD35-CRAC-01 | 2026-08-18 | THM-ELEC-02 | Loose electrical connection suspected; thermal hotspot confirmed by ultrasound arcing signature. | Thermal, Ultrasound | 78% | Warning | Under engineering review

## Recommendations_WorkOrders
Rec_ID | Alert_ID | Asset_ID | Recommended_Action | Urgency | Date_Issued | Work_Order_ID | WO_Status | Technician_Finding | Outcome | Date_Closed
REC-2001 | ALT-1001 | IAD35-CRAH-01 | Inspect and replace drive-side bearing within 2 weeks | High | 2026-08-15 | WO-3001 | Completed | Bearing wear confirmed on drive-side bearing; replaced during scheduled window. | True positive | 2026-08-19
REC-2002 | ALT-1002 | IAD35-CRAC-01 | Inspect electrical connections on Phase B within 1 week | High | 2026-08-18 | WO-3002 | Dispatched | Pending inspection | Pending