## New_Monitored_Assets
Asset_ID | Asset_Name | Site | Asset_Class | Sensors_Added | Register_Alert_Ref | Failure_Mode | Severity | Classification | Status
IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ashburn Campus - Building 35 | Pump (Chilled / Condenser Water) | Vibration, Ultrasound | ALT-0001 | V03 - Imbalance | High | True Positive | Closed - Resolved
ORD12-UPS-01 | UPS System 01 - ORD12 | Franklin Park Campus - Building 12 | UPS System | Thermal, Ultrasound | ALT-0002 | T01 - Loose Electrical Connection | Critical | True Positive | Closed - Resolved
LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | London Campus - Building 10 | LV Switchgear | Ultrasound, Thermal | ALT-0003 | U02 - Arcing | Critical | True Positive | Closed - Resolved
FRA15-XFMR-01 | Transformer 01 - FRA15 | Hanauer Landstrasse Campus - Building 15 | Transformer | Thermal, Ultrasound | ALT-0004 | T04 - Insulation Degradation (suspected) | High | Pending | Under Investigation
SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Loyang Campus - Building 11 | Standby Generator Set (parent asset) | Vibration, Thermal, Ultrasound | ALT-0005 | V02 - Misalignment | Medium | True Positive | Closed - Resolved
SYD12-CHIL-01 | Chiller 01 - SYD12 | Erskine Park Campus - Building 12 | Chiller | Vibration, Thermal, Ultrasound | ALT-0006 | V05 - Cavitation | Medium | False Positive | Closed - False Positive
ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Franklin Park Campus - Building 12 | PDU System (Power Distribution Unit) | Ultrasound, Thermal | ALT-0008 | U02 - Arcing | Low | Pending | Open
ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Franklin Park Campus - Building 12 | Air Handling Unit (AHU) | Vibration, Thermal | (new - not yet in register) | V04 - Looseness | Medium | Pending | Recommended
IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Ashburn Campus - Building 35 | Cooling Tower | Thermal, Vibration | (new - not yet in register) | T03 - Cooling Failure | High | Pending | Recommended
LHR10-UPS-01 | UPS System 01 - LHR10 | London Campus - Building 10 | UPS System | Thermal, Ultrasound | (new - not yet in register) | T02 - Overloaded Circuitry | Critical | Pending | Dispatched

## Sensor_Readings_Daily
Date | Asset_ID | Asset_Name | Sensor | Value | Unit | Alarm_Threshold | Status
2026-08-17 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 1.87 | mm/s RMS | 4.5 | Normal
2026-08-18 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.09 | mm/s RMS | 4.5 | Normal
2026-08-19 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 1.99 | mm/s RMS | 4.5 | Normal
2026-08-20 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.08 | mm/s RMS | 4.5 | Normal
2026-08-21 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.16 | mm/s RMS | 4.5 | Normal
2026-08-22 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.03 | mm/s RMS | 4.5 | Normal
2026-08-23 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.03 | mm/s RMS | 4.5 | Normal
2026-08-24 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 1.9 | mm/s RMS | 4.5 | Normal
2026-08-25 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 1.97 | mm/s RMS | 4.5 | Normal
2026-08-26 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.04 | mm/s RMS | 4.5 | Normal
2026-08-27 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.1 | mm/s RMS | 4.5 | Normal
2026-08-28 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.14 | mm/s RMS | 4.5 | Normal
2026-08-29 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.02 | mm/s RMS | 4.5 | Normal
2026-08-30 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 1.93 | mm/s RMS | 4.5 | Normal
2026-08-31 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2 | mm/s RMS | 4.5 | Normal
2026-09-01 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.19 | mm/s RMS | 4.5 | Normal
2026-09-02 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 1.99 | mm/s RMS | 4.5 | Normal
2026-09-03 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.06 | mm/s RMS | 4.5 | Normal
2026-09-04 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.21 | mm/s RMS | 4.5 | Normal
2026-09-05 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 1.94 | mm/s RMS | 4.5 | Normal
2026-09-06 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.12 | mm/s RMS | 4.5 | Normal
2026-09-07 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.23 | mm/s RMS | 4.5 | Normal
2026-09-08 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.02 | mm/s RMS | 4.5 | Normal
2026-09-09 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.64 | mm/s RMS | 4.5 | Normal
2026-09-10 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 3.28 | mm/s RMS | 4.5 | Normal
2026-09-11 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 3.58 | mm/s RMS | 4.5 | Normal
2026-09-12 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 4.22 | mm/s RMS | 4.5 | Elevated
2026-09-13 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 4.82 | mm/s RMS | 4.5 | Alarm
2026-09-14 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 5.32 | mm/s RMS | 4.5 | Alarm
2026-09-15 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 5.79 | mm/s RMS | 4.5 | Alarm
2026-09-16 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 4.58 | mm/s RMS | 4.5 | Alarm
2026-09-17 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 3.53 | mm/s RMS | 4.5 | Normal
2026-09-18 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Vibration | 2.36 | mm/s RMS | 4.5 | Normal
2026-08-17 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 15.95 | dB uV | 38 | Normal
2026-08-18 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 15.78 | dB uV | 38 | Normal
2026-08-19 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16.77 | dB uV | 38 | Normal
2026-08-20 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16.67 | dB uV | 38 | Normal
2026-08-21 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 15.81 | dB uV | 38 | Normal
2026-08-22 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16.37 | dB uV | 38 | Normal
2026-08-23 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 15.82 | dB uV | 38 | Normal
2026-08-24 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16.22 | dB uV | 38 | Normal
2026-08-25 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16.07 | dB uV | 38 | Normal
2026-08-26 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16.72 | dB uV | 38 | Normal
2026-08-27 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16.2 | dB uV | 38 | Normal
2026-08-28 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16.42 | dB uV | 38 | Normal
2026-08-29 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16.98 | dB uV | 38 | Normal
2026-08-30 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16.42 | dB uV | 38 | Normal
2026-08-31 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 17.45 | dB uV | 38 | Normal
2026-09-01 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16.04 | dB uV | 38 | Normal
2026-09-02 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 17.21 | dB uV | 38 | Normal
2026-09-03 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16.62 | dB uV | 38 | Normal
2026-09-04 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16.67 | dB uV | 38 | Normal
2026-09-05 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 17.13 | dB uV | 38 | Normal
2026-09-06 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16.95 | dB uV | 38 | Normal
2026-09-07 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16.78 | dB uV | 38 | Normal
2026-09-08 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16 | dB uV | 38 | Normal
2026-09-09 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 17.18 | dB uV | 38 | Normal
2026-09-10 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 19.42 | dB uV | 38 | Normal
2026-09-11 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 20.05 | dB uV | 38 | Normal
2026-09-12 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 21.39 | dB uV | 38 | Normal
2026-09-13 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 22.91 | dB uV | 38 | Normal
2026-09-14 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 23.37 | dB uV | 38 | Normal
2026-09-15 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 23.11 | dB uV | 38 | Normal
2026-09-16 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 21.28 | dB uV | 38 | Normal
2026-09-17 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 19.52 | dB uV | 38 | Normal
2026-09-18 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Ultrasound | 16.47 | dB uV | 38 | Normal
2026-08-22 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 45.12 | degC | 59 | Normal
2026-08-23 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 45.16 | degC | 59 | Normal
2026-08-24 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 45.03 | degC | 59 | Normal
2026-08-25 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 44.22 | degC | 59 | Normal
2026-08-26 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 45.2 | degC | 59 | Normal
2026-08-27 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 43.59 | degC | 59 | Normal
2026-08-28 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 44.11 | degC | 59 | Normal
2026-08-29 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 44.58 | degC | 59 | Normal
2026-08-30 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 45.34 | degC | 59 | Normal
2026-08-31 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 44.82 | degC | 59 | Normal
2026-09-01 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 44.08 | degC | 59 | Normal
2026-09-02 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 44.67 | degC | 59 | Normal
2026-09-03 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 44.72 | degC | 59 | Normal
2026-09-04 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 44.76 | degC | 59 | Normal
2026-09-05 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 44.53 | degC | 59 | Normal
2026-09-06 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 45.22 | degC | 59 | Normal
2026-09-07 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 45.4 | degC | 59 | Normal
2026-09-08 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 46.28 | degC | 59 | Normal
2026-09-09 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 46.43 | degC | 59 | Normal
2026-09-10 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 45.86 | degC | 59 | Normal
2026-09-11 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 45.81 | degC | 59 | Normal
2026-09-12 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 46.67 | degC | 59 | Normal
2026-09-13 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 49.68 | degC | 59 | Normal
2026-09-14 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 51.92 | degC | 59 | Elevated
2026-09-15 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 54.97 | degC | 59 | Elevated
2026-09-16 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 58.05 | degC | 59 | Elevated
2026-09-17 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 58.65 | degC | 59 | Elevated
2026-09-18 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 63.4 | degC | 59 | Alarm
2026-09-19 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 64.71 | degC | 59 | Alarm
2026-09-20 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 67.94 | degC | 59 | Alarm
2026-09-21 | ORD12-UPS-01 | UPS System 01 - ORD12 | Thermal | 45.71 | degC | 59 | Normal
2026-08-22 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 14.43 | dB uV | 38 | Normal
2026-08-23 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 13.34 | dB uV | 38 | Normal
2026-08-24 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 14.41 | dB uV | 38 | Normal
2026-08-25 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 13.28 | dB uV | 38 | Normal
2026-08-26 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 13.9 | dB uV | 38 | Normal
2026-08-27 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 14.86 | dB uV | 38 | Normal
2026-08-28 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 14.14 | dB uV | 38 | Normal
2026-08-29 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 14.53 | dB uV | 38 | Normal
2026-08-30 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 14.84 | dB uV | 38 | Normal
2026-08-31 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 15.07 | dB uV | 38 | Normal
2026-09-01 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 15 | dB uV | 38 | Normal
2026-09-02 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 13.54 | dB uV | 38 | Normal
2026-09-03 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 14.41 | dB uV | 38 | Normal
2026-09-04 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 14.55 | dB uV | 38 | Normal
2026-09-05 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 13.78 | dB uV | 38 | Normal
2026-09-06 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 14.8 | dB uV | 38 | Normal
2026-09-07 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 14.98 | dB uV | 38 | Normal
2026-09-08 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 15.47 | dB uV | 38 | Normal
2026-09-09 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 15.74 | dB uV | 38 | Normal
2026-09-10 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 14.16 | dB uV | 38 | Normal
2026-09-11 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 14.41 | dB uV | 38 | Normal
2026-09-12 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 15.32 | dB uV | 38 | Normal
2026-09-13 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 15.14 | dB uV | 38 | Normal
2026-09-14 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 16.2 | dB uV | 38 | Normal
2026-09-15 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 17.77 | dB uV | 38 | Normal
2026-09-16 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 17.84 | dB uV | 38 | Normal
2026-09-17 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 19.94 | dB uV | 38 | Normal
2026-09-18 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 20.96 | dB uV | 38 | Normal
2026-09-19 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 20.19 | dB uV | 38 | Normal
2026-09-20 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 22.07 | dB uV | 38 | Normal
2026-09-21 | ORD12-UPS-01 | UPS System 01 - ORD12 | Ultrasound | 15.59 | dB uV | 38 | Normal
2026-08-29 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 18.14 | dB uV | 38 | Normal
2026-08-30 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 16.5 | dB uV | 38 | Normal
2026-08-31 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 16.3 | dB uV | 38 | Normal
2026-09-01 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 18.04 | dB uV | 38 | Normal
2026-09-02 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 18.16 | dB uV | 38 | Normal
2026-09-03 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 16.5 | dB uV | 38 | Normal
2026-09-04 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 17.13 | dB uV | 38 | Normal
2026-09-05 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 17.84 | dB uV | 38 | Normal
2026-09-06 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 18.19 | dB uV | 38 | Normal
2026-09-07 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 16.61 | dB uV | 38 | Normal
2026-09-08 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 17.85 | dB uV | 38 | Normal
2026-09-09 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 18.24 | dB uV | 38 | Normal
2026-09-10 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 17.66 | dB uV | 38 | Normal
2026-09-11 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 16.79 | dB uV | 38 | Normal
2026-09-12 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 16.52 | dB uV | 38 | Normal
2026-09-13 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 17.16 | dB uV | 38 | Normal
2026-09-14 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 18.47 | dB uV | 38 | Normal
2026-09-15 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 16.68 | dB uV | 38 | Normal
2026-09-16 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 16.64 | dB uV | 38 | Normal
2026-09-17 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 17.53 | dB uV | 38 | Normal
2026-09-18 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 16.86 | dB uV | 38 | Normal
2026-09-19 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 17.11 | dB uV | 38 | Normal
2026-09-20 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 16.86 | dB uV | 38 | Normal
2026-09-21 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 21.35 | dB uV | 38 | Normal
2026-09-22 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 25.04 | dB uV | 38 | Normal
2026-09-23 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 27.68 | dB uV | 38 | Normal
2026-09-24 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 30.27 | dB uV | 38 | Normal
2026-09-25 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 34.02 | dB uV | 38 | Elevated
2026-09-26 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 37.93 | dB uV | 38 | Elevated
2026-09-27 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 42.06 | dB uV | 38 | Alarm
2026-09-28 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 30.68 | dB uV | 38 | Normal
2026-09-29 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Ultrasound | 17.38 | dB uV | 38 | Normal
2026-08-29 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 31.02 | degC | 55 | Normal
2026-08-30 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 32.71 | degC | 55 | Normal
2026-08-31 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 32.94 | degC | 55 | Normal
2026-09-01 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 32.05 | degC | 55 | Normal
2026-09-02 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 32.72 | degC | 55 | Normal
2026-09-03 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 32.96 | degC | 55 | Normal
2026-09-04 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 32.49 | degC | 55 | Normal
2026-09-05 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 33.06 | degC | 55 | Normal
2026-09-06 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 31.41 | degC | 55 | Normal
2026-09-07 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 31.95 | degC | 55 | Normal
2026-09-08 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 32.01 | degC | 55 | Normal
2026-09-09 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 31.74 | degC | 55 | Normal
2026-09-10 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 33.37 | degC | 55 | Normal
2026-09-11 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 31.65 | degC | 55 | Normal
2026-09-12 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 32.98 | degC | 55 | Normal
2026-09-13 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 31.82 | degC | 55 | Normal
2026-09-14 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 32.45 | degC | 55 | Normal
2026-09-15 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 32.61 | degC | 55 | Normal
2026-09-16 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 32.18 | degC | 55 | Normal
2026-09-17 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 32.91 | degC | 55 | Normal
2026-09-18 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 32.98 | degC | 55 | Normal
2026-09-19 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 32.59 | degC | 55 | Normal
2026-09-20 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 33.47 | degC | 55 | Normal
2026-09-21 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 33.32 | degC | 55 | Normal
2026-09-22 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 34.39 | degC | 55 | Normal
2026-09-23 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 35.71 | degC | 55 | Normal
2026-09-24 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 36.76 | degC | 55 | Normal
2026-09-25 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 37.41 | degC | 55 | Normal
2026-09-26 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 39.84 | degC | 55 | Normal
2026-09-27 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 40.66 | degC | 55 | Normal
2026-09-28 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 35.71 | degC | 55 | Normal
2026-09-29 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Thermal | 32.74 | degC | 55 | Normal
2026-09-03 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 60.3 | degC | 76 | Normal
2026-09-04 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 60.99 | degC | 76 | Normal
2026-09-05 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 60.65 | degC | 76 | Normal
2026-09-06 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 61.36 | degC | 76 | Normal
2026-09-07 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 62.57 | degC | 76 | Normal
2026-09-08 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 61.28 | degC | 76 | Normal
2026-09-09 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 62.1 | degC | 76 | Normal
2026-09-10 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 62.07 | degC | 76 | Normal
2026-09-11 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 62.6 | degC | 76 | Normal
2026-09-12 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 60.92 | degC | 76 | Normal
2026-09-13 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 62.81 | degC | 76 | Normal
2026-09-14 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 63.45 | degC | 76 | Normal
2026-09-15 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 62.68 | degC | 76 | Normal
2026-09-16 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 61.98 | degC | 76 | Normal
2026-09-17 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 63.1 | degC | 76 | Normal
2026-09-18 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 63.32 | degC | 76 | Normal
2026-09-19 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 63.29 | degC | 76 | Normal
2026-09-20 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 62.08 | degC | 76 | Normal
2026-09-21 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 65.56 | degC | 76 | Elevated
2026-09-22 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 66.85 | degC | 76 | Elevated
2026-09-23 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 66.8 | degC | 76 | Elevated
2026-09-24 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 68.58 | degC | 76 | Elevated
2026-09-25 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 68.47 | degC | 76 | Elevated
2026-09-26 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 72.27 | degC | 76 | Elevated
2026-09-27 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 73.16 | degC | 76 | Elevated
2026-09-28 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 74.02 | degC | 76 | Elevated
2026-09-29 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 75.68 | degC | 76 | Elevated
2026-09-30 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 75.52 | degC | 76 | Elevated
2026-10-01 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 77.17 | degC | 76 | Alarm
2026-10-02 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Thermal | 78.34 | degC | 76 | Alarm
2026-09-03 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 19.19 | dB uV | 38 | Normal
2026-09-04 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 18.24 | dB uV | 38 | Normal
2026-09-05 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 19.91 | dB uV | 38 | Normal
2026-09-06 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 19.1 | dB uV | 38 | Normal
2026-09-07 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 19.12 | dB uV | 38 | Normal
2026-09-08 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 18.5 | dB uV | 38 | Normal
2026-09-09 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 19.72 | dB uV | 38 | Normal
2026-09-10 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 20.05 | dB uV | 38 | Normal
2026-09-11 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 19.73 | dB uV | 38 | Normal
2026-09-12 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 19.01 | dB uV | 38 | Normal
2026-09-13 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 20.16 | dB uV | 38 | Normal
2026-09-14 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 18.94 | dB uV | 38 | Normal
2026-09-15 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 20.36 | dB uV | 38 | Normal
2026-09-16 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 19.93 | dB uV | 38 | Normal
2026-09-17 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 19.4 | dB uV | 38 | Normal
2026-09-18 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 19.91 | dB uV | 38 | Normal
2026-09-19 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 20.2 | dB uV | 38 | Normal
2026-09-20 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 19.52 | dB uV | 38 | Normal
2026-09-21 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 21.44 | dB uV | 38 | Normal
2026-09-22 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 21.34 | dB uV | 38 | Normal
2026-09-23 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 23.03 | dB uV | 38 | Normal
2026-09-24 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 23.67 | dB uV | 38 | Normal
2026-09-25 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 22.95 | dB uV | 38 | Normal
2026-09-26 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 24.79 | dB uV | 38 | Normal
2026-09-27 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 24.87 | dB uV | 38 | Normal
2026-09-28 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 26.51 | dB uV | 38 | Normal
2026-09-29 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 26.84 | dB uV | 38 | Normal
2026-09-30 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 27.42 | dB uV | 38 | Normal
2026-10-01 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 29.04 | dB uV | 38 | Normal
2026-10-02 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Ultrasound | 28.11 | dB uV | 38 | Normal
2026-09-06 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.72 | mm/s RMS | 3.5 | Normal
2026-09-07 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.66 | mm/s RMS | 3.5 | Normal
2026-09-08 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.58 | mm/s RMS | 3.5 | Normal
2026-09-09 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.8 | mm/s RMS | 3.5 | Normal
2026-09-10 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.75 | mm/s RMS | 3.5 | Normal
2026-09-11 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.86 | mm/s RMS | 3.5 | Normal
2026-09-12 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.78 | mm/s RMS | 3.5 | Normal
2026-09-13 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.71 | mm/s RMS | 3.5 | Normal
2026-09-14 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.92 | mm/s RMS | 3.5 | Normal
2026-09-15 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.67 | mm/s RMS | 3.5 | Normal
2026-09-16 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.66 | mm/s RMS | 3.5 | Normal
2026-09-17 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.87 | mm/s RMS | 3.5 | Normal
2026-09-18 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.77 | mm/s RMS | 3.5 | Normal
2026-09-19 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.78 | mm/s RMS | 3.5 | Normal
2026-09-20 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.94 | mm/s RMS | 3.5 | Normal
2026-09-21 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.78 | mm/s RMS | 3.5 | Normal
2026-09-22 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.96 | mm/s RMS | 3.5 | Normal
2026-09-23 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.9 | mm/s RMS | 3.5 | Normal
2026-09-24 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.81 | mm/s RMS | 3.5 | Normal
2026-09-25 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.74 | mm/s RMS | 3.5 | Normal
2026-09-26 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.81 | mm/s RMS | 3.5 | Normal
2026-09-27 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 2.03 | mm/s RMS | 3.5 | Normal
2026-09-28 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.87 | mm/s RMS | 3.5 | Normal
2026-09-29 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 2.08 | mm/s RMS | 3.5 | Normal
2026-09-30 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 2.41 | mm/s RMS | 3.5 | Normal
2026-10-01 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 2.88 | mm/s RMS | 3.5 | Normal
2026-10-02 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 2.94 | mm/s RMS | 3.5 | Normal
2026-10-03 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 3.41 | mm/s RMS | 3.5 | Elevated
2026-10-04 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 3.5 | mm/s RMS | 3.5 | Alarm
2026-10-05 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 4.04 | mm/s RMS | 3.5 | Alarm
2026-10-06 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Vibration | 1.81 | mm/s RMS | 3.5 | Normal
2026-09-06 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 54.09 | degC | 70 | Normal
2026-09-07 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 55.86 | degC | 70 | Normal
2026-09-08 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 54.72 | degC | 70 | Normal
2026-09-09 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 55.46 | degC | 70 | Normal
2026-09-10 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 55.05 | degC | 70 | Normal
2026-09-11 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 54.19 | degC | 70 | Normal
2026-09-12 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 54.21 | degC | 70 | Normal
2026-09-13 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 54.3 | degC | 70 | Normal
2026-09-14 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 54.32 | degC | 70 | Normal
2026-09-15 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 54.11 | degC | 70 | Normal
2026-09-16 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 54.09 | degC | 70 | Normal
2026-09-17 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 55.9 | degC | 70 | Normal
2026-09-18 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 54.18 | degC | 70 | Normal
2026-09-19 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 55.02 | degC | 70 | Normal
2026-09-20 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 54.24 | degC | 70 | Normal
2026-09-21 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 54.43 | degC | 70 | Normal
2026-09-22 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 55.53 | degC | 70 | Normal
2026-09-23 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 55.88 | degC | 70 | Normal
2026-09-24 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 54.94 | degC | 70 | Normal
2026-09-25 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 54.01 | degC | 70 | Normal
2026-09-26 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 56 | degC | 70 | Normal
2026-09-27 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 54.1 | degC | 70 | Normal
2026-09-28 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 54.78 | degC | 70 | Normal
2026-09-29 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 55.36 | degC | 70 | Normal
2026-09-30 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 56.35 | degC | 70 | Normal
2026-10-01 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 56.5 | degC | 70 | Normal
2026-10-02 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 56.36 | degC | 70 | Normal
2026-10-03 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 56.23 | degC | 70 | Normal
2026-10-04 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 57.38 | degC | 70 | Normal
2026-10-05 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 57.74 | degC | 70 | Normal
2026-10-06 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Thermal | 55.74 | degC | 70 | Normal
2026-09-06 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 16.44 | dB uV | 38 | Normal
2026-09-07 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 15.2 | dB uV | 38 | Normal
2026-09-08 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 15.6 | dB uV | 38 | Normal
2026-09-09 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 15.97 | dB uV | 38 | Normal
2026-09-10 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 16.01 | dB uV | 38 | Normal
2026-09-11 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 16.67 | dB uV | 38 | Normal
2026-09-12 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 15.48 | dB uV | 38 | Normal
2026-09-13 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 16.33 | dB uV | 38 | Normal
2026-09-14 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 15.75 | dB uV | 38 | Normal
2026-09-15 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 16.55 | dB uV | 38 | Normal
2026-09-16 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 15.39 | dB uV | 38 | Normal
2026-09-17 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 15.95 | dB uV | 38 | Normal
2026-09-18 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 15.21 | dB uV | 38 | Normal
2026-09-19 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 15.42 | dB uV | 38 | Normal
2026-09-20 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 16.87 | dB uV | 38 | Normal
2026-09-21 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 15.63 | dB uV | 38 | Normal
2026-09-22 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 16.79 | dB uV | 38 | Normal
2026-09-23 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 16.05 | dB uV | 38 | Normal
2026-09-24 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 15.08 | dB uV | 38 | Normal
2026-09-25 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 16.59 | dB uV | 38 | Normal
2026-09-26 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 15.1 | dB uV | 38 | Normal
2026-09-27 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 16.65 | dB uV | 38 | Normal
2026-09-28 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 15.02 | dB uV | 38 | Normal
2026-09-29 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 16.63 | dB uV | 38 | Normal
2026-09-30 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 15.9 | dB uV | 38 | Normal
2026-10-01 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 16.54 | dB uV | 38 | Normal
2026-10-02 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 18.05 | dB uV | 38 | Normal
2026-10-03 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 17.4 | dB uV | 38 | Normal
2026-10-04 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 18.03 | dB uV | 38 | Normal
2026-10-05 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 18.48 | dB uV | 38 | Normal
2026-10-06 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Ultrasound | 15.22 | dB uV | 38 | Normal
2026-09-10 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 2 | mm/s RMS | 3.5 | Normal
2026-09-11 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 2.03 | mm/s RMS | 3.5 | Normal
2026-09-12 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 1.81 | mm/s RMS | 3.5 | Normal
2026-09-13 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 1.93 | mm/s RMS | 3.5 | Normal
2026-09-14 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 1.85 | mm/s RMS | 3.5 | Normal
2026-09-15 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 2 | mm/s RMS | 3.5 | Normal
2026-09-16 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 1.79 | mm/s RMS | 3.5 | Normal
2026-09-17 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 1.94 | mm/s RMS | 3.5 | Normal
2026-09-18 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 2.03 | mm/s RMS | 3.5 | Normal
2026-09-19 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 2.01 | mm/s RMS | 3.5 | Normal
2026-09-20 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 1.83 | mm/s RMS | 3.5 | Normal
2026-09-21 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 2.05 | mm/s RMS | 3.5 | Normal
2026-09-22 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 1.88 | mm/s RMS | 3.5 | Normal
2026-09-23 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 2.05 | mm/s RMS | 3.5 | Normal
2026-09-24 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 1.97 | mm/s RMS | 3.5 | Normal
2026-09-25 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 1.87 | mm/s RMS | 3.5 | Normal
2026-09-26 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 2.05 | mm/s RMS | 3.5 | Normal
2026-09-27 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 2.07 | mm/s RMS | 3.5 | Normal
2026-09-28 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 2.05 | mm/s RMS | 3.5 | Normal
2026-09-29 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 2.13 | mm/s RMS | 3.5 | Normal
2026-09-30 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 1.92 | mm/s RMS | 3.5 | Normal
2026-10-01 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 1.92 | mm/s RMS | 3.5 | Normal
2026-10-02 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 2.09 | mm/s RMS | 3.5 | Normal
2026-10-03 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 2.41 | mm/s RMS | 3.5 | Normal
2026-10-04 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 2.57 | mm/s RMS | 3.5 | Normal
2026-10-05 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 2.76 | mm/s RMS | 3.5 | Normal
2026-10-06 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 2.99 | mm/s RMS | 3.5 | Elevated
2026-10-07 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 3.13 | mm/s RMS | 3.5 | Elevated
2026-10-08 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 3.25 | mm/s RMS | 3.5 | Elevated
2026-10-09 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Vibration | 3.59 | mm/s RMS | 3.5 | Alarm
2026-09-10 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 27.73 | degC | 41 | Normal
2026-09-11 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 27.94 | degC | 41 | Normal
2026-09-12 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.51 | degC | 41 | Normal
2026-09-13 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 27.61 | degC | 41 | Normal
2026-09-14 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.16 | degC | 41 | Normal
2026-09-15 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.17 | degC | 41 | Normal
2026-09-16 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 27.74 | degC | 41 | Normal
2026-09-17 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 27.97 | degC | 41 | Normal
2026-09-18 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.56 | degC | 41 | Normal
2026-09-19 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 27.81 | degC | 41 | Normal
2026-09-20 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.25 | degC | 41 | Normal
2026-09-21 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.41 | degC | 41 | Normal
2026-09-22 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 27.83 | degC | 41 | Normal
2026-09-23 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.59 | degC | 41 | Normal
2026-09-24 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.15 | degC | 41 | Normal
2026-09-25 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28 | degC | 41 | Normal
2026-09-26 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.26 | degC | 41 | Normal
2026-09-27 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 27.91 | degC | 41 | Normal
2026-09-28 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.25 | degC | 41 | Normal
2026-09-29 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 27.73 | degC | 41 | Normal
2026-09-30 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.51 | degC | 41 | Normal
2026-10-01 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.05 | degC | 41 | Normal
2026-10-02 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 27.73 | degC | 41 | Normal
2026-10-03 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28 | degC | 41 | Normal
2026-10-04 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.59 | degC | 41 | Normal
2026-10-05 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.52 | degC | 41 | Normal
2026-10-06 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.17 | degC | 41 | Normal
2026-10-07 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.05 | degC | 41 | Normal
2026-10-08 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.11 | degC | 41 | Normal
2026-10-09 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Thermal | 28.88 | degC | 41 | Normal
2026-09-10 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 16.38 | dB uV | 34 | Normal
2026-09-11 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.62 | dB uV | 34 | Normal
2026-09-12 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.57 | dB uV | 34 | Normal
2026-09-13 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 16.56 | dB uV | 34 | Normal
2026-09-14 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 16.76 | dB uV | 34 | Normal
2026-09-15 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.11 | dB uV | 34 | Normal
2026-09-16 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.48 | dB uV | 34 | Normal
2026-09-17 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.72 | dB uV | 34 | Normal
2026-09-18 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.79 | dB uV | 34 | Normal
2026-09-19 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 16.65 | dB uV | 34 | Normal
2026-09-20 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 16.51 | dB uV | 34 | Normal
2026-09-21 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 16.98 | dB uV | 34 | Normal
2026-09-22 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.09 | dB uV | 34 | Normal
2026-09-23 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.25 | dB uV | 34 | Normal
2026-09-24 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 16.37 | dB uV | 34 | Normal
2026-09-25 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.23 | dB uV | 34 | Normal
2026-09-26 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.67 | dB uV | 34 | Normal
2026-09-27 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.66 | dB uV | 34 | Normal
2026-09-28 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.71 | dB uV | 34 | Normal
2026-09-29 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.68 | dB uV | 34 | Normal
2026-09-30 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.74 | dB uV | 34 | Normal
2026-10-01 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 16.28 | dB uV | 34 | Normal
2026-10-02 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.73 | dB uV | 34 | Normal
2026-10-03 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 16.76 | dB uV | 34 | Normal
2026-10-04 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 16.9 | dB uV | 34 | Normal
2026-10-05 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.18 | dB uV | 34 | Normal
2026-10-06 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 18.04 | dB uV | 34 | Normal
2026-10-07 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.54 | dB uV | 34 | Normal
2026-10-08 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.2 | dB uV | 34 | Normal
2026-10-09 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Ultrasound | 17.3 | dB uV | 34 | Normal
2026-09-19 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 15.81 | dB uV | 38 | Normal
2026-09-20 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 15.71 | dB uV | 38 | Normal
2026-09-21 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 14.4 | dB uV | 38 | Normal
2026-09-22 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 14.68 | dB uV | 38 | Normal
2026-09-23 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 14.99 | dB uV | 38 | Normal
2026-09-24 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 14.75 | dB uV | 38 | Normal
2026-09-25 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 15.5 | dB uV | 38 | Normal
2026-09-26 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 14.88 | dB uV | 38 | Normal
2026-09-27 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 15.65 | dB uV | 38 | Normal
2026-09-28 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 16.43 | dB uV | 38 | Normal
2026-09-29 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 16.32 | dB uV | 38 | Normal
2026-09-30 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 14.89 | dB uV | 38 | Normal
2026-10-01 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 15.16 | dB uV | 38 | Normal
2026-10-02 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 15.64 | dB uV | 38 | Normal
2026-10-03 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 16.17 | dB uV | 38 | Normal
2026-10-04 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 15.71 | dB uV | 38 | Normal
2026-10-05 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 15.5 | dB uV | 38 | Normal
2026-10-06 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 16.3 | dB uV | 38 | Normal
2026-10-07 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 16.64 | dB uV | 38 | Normal
2026-10-08 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 18.57 | dB uV | 38 | Normal
2026-10-09 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 18.86 | dB uV | 38 | Normal
2026-10-10 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 18.9 | dB uV | 38 | Normal
2026-10-11 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 20.09 | dB uV | 38 | Normal
2026-10-12 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 20.35 | dB uV | 38 | Normal
2026-10-13 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 20.98 | dB uV | 38 | Normal
2026-10-14 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 21.27 | dB uV | 38 | Normal
2026-10-15 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 22.13 | dB uV | 38 | Normal
2026-10-16 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 23.74 | dB uV | 38 | Normal
2026-10-17 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 23.95 | dB uV | 38 | Normal
2026-10-18 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Ultrasound | 24.66 | dB uV | 38 | Normal
2026-09-19 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 31.4 | degC | 55 | Normal
2026-09-20 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 32.01 | degC | 55 | Normal
2026-09-21 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 31.79 | degC | 55 | Normal
2026-09-22 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 31.34 | degC | 55 | Normal
2026-09-23 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 31.83 | degC | 55 | Normal
2026-09-24 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 31.32 | degC | 55 | Normal
2026-09-25 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 31.57 | degC | 55 | Normal
2026-09-26 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 32.48 | degC | 55 | Normal
2026-09-27 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 32.3 | degC | 55 | Normal
2026-09-28 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 32.32 | degC | 55 | Normal
2026-09-29 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 31.33 | degC | 55 | Normal
2026-09-30 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 31.46 | degC | 55 | Normal
2026-10-01 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 31.23 | degC | 55 | Normal
2026-10-02 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 31.36 | degC | 55 | Normal
2026-10-03 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 31.36 | degC | 55 | Normal
2026-10-04 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 32.74 | degC | 55 | Normal
2026-10-05 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 32.63 | degC | 55 | Normal
2026-10-06 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 31.68 | degC | 55 | Normal
2026-10-07 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 31.91 | degC | 55 | Normal
2026-10-08 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 33.2 | degC | 55 | Normal
2026-10-09 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 32.73 | degC | 55 | Normal
2026-10-10 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 32.56 | degC | 55 | Normal
2026-10-11 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 32.87 | degC | 55 | Normal
2026-10-12 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 32.71 | degC | 55 | Normal
2026-10-13 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 33.36 | degC | 55 | Normal
2026-10-14 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 33.75 | degC | 55 | Normal
2026-10-15 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 33.56 | degC | 55 | Normal
2026-10-16 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 34.21 | degC | 55 | Normal
2026-10-17 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 33.23 | degC | 55 | Normal
2026-10-18 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Thermal | 34.17 | degC | 55 | Normal
2026-08-10 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Vibration | 1.75 | mm/s RMS | 3.5 | Normal
2026-08-11 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Vibration | 1.52 | mm/s RMS | 3.5 | Normal
2026-08-12 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Vibration | 1.66 | mm/s RMS | 3.5 | Normal
2026-08-13 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Vibration | 1.72 | mm/s RMS | 3.5 | Normal
2026-08-14 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Vibration | 1.67 | mm/s RMS | 3.5 | Normal
2026-08-15 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Vibration | 1.88 | mm/s RMS | 3.5 | Normal
2026-08-16 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Vibration | 1.77 | mm/s RMS | 3.5 | Normal
2026-08-17 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Vibration | 1.79 | mm/s RMS | 3.5 | Normal
2026-08-18 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Vibration | 2.15 | mm/s RMS | 3.5 | Normal
2026-08-19 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Vibration | 2.11 | mm/s RMS | 3.5 | Normal
2026-08-20 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Vibration | 2.6 | mm/s RMS | 3.5 | Normal
2026-08-21 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Vibration | 2.6 | mm/s RMS | 3.5 | Normal
2026-08-22 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Vibration | 2.91 | mm/s RMS | 3.5 | Normal
2026-08-23 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Vibration | 3.17 | mm/s RMS | 3.5 | Elevated
2026-08-24 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Vibration | 3.39 | mm/s RMS | 3.5 | Elevated
2026-08-10 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Thermal | 29.36 | degC | 45 | Normal
2026-08-11 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Thermal | 29.74 | degC | 45 | Normal
2026-08-12 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Thermal | 29.8 | degC | 45 | Normal
2026-08-13 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Thermal | 30.64 | degC | 45 | Normal
2026-08-14 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Thermal | 30.58 | degC | 45 | Normal
2026-08-15 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Thermal | 30.12 | degC | 45 | Normal
2026-08-16 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Thermal | 30.61 | degC | 45 | Normal
2026-08-17 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Thermal | 30.51 | degC | 45 | Normal
2026-08-18 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Thermal | 29.9 | degC | 45 | Normal
2026-08-19 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Thermal | 29.61 | degC | 45 | Normal
2026-08-20 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Thermal | 30.36 | degC | 45 | Normal
2026-08-21 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Thermal | 30.04 | degC | 45 | Normal
2026-08-22 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Thermal | 29.67 | degC | 45 | Normal
2026-08-23 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Thermal | 31.1 | degC | 45 | Normal
2026-08-24 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Thermal | 31.16 | degC | 45 | Normal
2026-08-10 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Thermal | 29.06 | degC | 42 | Normal
2026-08-11 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Thermal | 29.33 | degC | 42 | Normal
2026-08-12 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Thermal | 29.56 | degC | 42 | Normal
2026-08-13 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Thermal | 30.11 | degC | 42 | Normal
2026-08-14 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Thermal | 29.52 | degC | 42 | Normal
2026-08-15 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Thermal | 29.85 | degC | 42 | Normal
2026-08-16 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Thermal | 29.42 | degC | 42 | Normal
2026-08-17 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Thermal | 29.59 | degC | 42 | Normal
2026-08-18 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Thermal | 31.32 | degC | 42 | Normal
2026-08-19 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Thermal | 32.14 | degC | 42 | Normal
2026-08-20 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Thermal | 33.11 | degC | 42 | Normal
2026-08-21 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Thermal | 34.93 | degC | 42 | Normal
2026-08-22 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Thermal | 36.83 | degC | 42 | Elevated
2026-08-23 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Thermal | 37.36 | degC | 42 | Elevated
2026-08-24 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Thermal | 39.58 | degC | 42 | Elevated
2026-08-10 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Vibration | 1.76 | mm/s RMS | 3.5 | Normal
2026-08-11 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Vibration | 1.75 | mm/s RMS | 3.5 | Normal
2026-08-12 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Vibration | 1.82 | mm/s RMS | 3.5 | Normal
2026-08-13 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Vibration | 1.57 | mm/s RMS | 3.5 | Normal
2026-08-14 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Vibration | 1.6 | mm/s RMS | 3.5 | Normal
2026-08-15 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Vibration | 1.82 | mm/s RMS | 3.5 | Normal
2026-08-16 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Vibration | 1.82 | mm/s RMS | 3.5 | Normal
2026-08-17 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Vibration | 1.57 | mm/s RMS | 3.5 | Normal
2026-08-18 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Vibration | 1.81 | mm/s RMS | 3.5 | Normal
2026-08-19 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Vibration | 1.61 | mm/s RMS | 3.5 | Normal
2026-08-20 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Vibration | 1.68 | mm/s RMS | 3.5 | Normal
2026-08-21 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Vibration | 1.7 | mm/s RMS | 3.5 | Normal
2026-08-22 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Vibration | 1.78 | mm/s RMS | 3.5 | Normal
2026-08-23 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Vibration | 1.84 | mm/s RMS | 3.5 | Normal
2026-08-24 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Vibration | 2.02 | mm/s RMS | 3.5 | Normal
2026-08-10 | LHR10-UPS-01 | UPS System 01 - LHR10 | Thermal | 42.86 | degC | 59 | Normal
2026-08-11 | LHR10-UPS-01 | UPS System 01 - LHR10 | Thermal | 42.46 | degC | 59 | Normal
2026-08-12 | LHR10-UPS-01 | UPS System 01 - LHR10 | Thermal | 43.07 | degC | 59 | Normal
2026-08-13 | LHR10-UPS-01 | UPS System 01 - LHR10 | Thermal | 42.77 | degC | 59 | Normal
2026-08-14 | LHR10-UPS-01 | UPS System 01 - LHR10 | Thermal | 43.1 | degC | 59 | Normal
2026-08-15 | LHR10-UPS-01 | UPS System 01 - LHR10 | Thermal | 44.28 | degC | 59 | Normal
2026-08-16 | LHR10-UPS-01 | UPS System 01 - LHR10 | Thermal | 44.74 | degC | 59 | Normal
2026-08-17 | LHR10-UPS-01 | UPS System 01 - LHR10 | Thermal | 44.45 | degC | 59 | Normal
2026-08-18 | LHR10-UPS-01 | UPS System 01 - LHR10 | Thermal | 47.02 | degC | 59 | Normal
2026-08-19 | LHR10-UPS-01 | UPS System 01 - LHR10 | Thermal | 48.7 | degC | 59 | Normal
2026-08-20 | LHR10-UPS-01 | UPS System 01 - LHR10 | Thermal | 52.21 | degC | 59 | Elevated
2026-08-21 | LHR10-UPS-01 | UPS System 01 - LHR10 | Thermal | 53.91 | degC | 59 | Elevated
2026-08-22 | LHR10-UPS-01 | UPS System 01 - LHR10 | Thermal | 55.68 | degC | 59 | Elevated
2026-08-23 | LHR10-UPS-01 | UPS System 01 - LHR10 | Thermal | 58.71 | degC | 59 | Elevated
2026-08-24 | LHR10-UPS-01 | UPS System 01 - LHR10 | Thermal | 60.36 | degC | 59 | Alarm
2026-08-10 | LHR10-UPS-01 | UPS System 01 - LHR10 | Ultrasound | 13.58 | dB uV | 38 | Normal
2026-08-11 | LHR10-UPS-01 | UPS System 01 - LHR10 | Ultrasound | 13.39 | dB uV | 38 | Normal
2026-08-12 | LHR10-UPS-01 | UPS System 01 - LHR10 | Ultrasound | 14.85 | dB uV | 38 | Normal
2026-08-13 | LHR10-UPS-01 | UPS System 01 - LHR10 | Ultrasound | 13.99 | dB uV | 38 | Normal
2026-08-14 | LHR10-UPS-01 | UPS System 01 - LHR10 | Ultrasound | 15.48 | dB uV | 38 | Normal
2026-08-15 | LHR10-UPS-01 | UPS System 01 - LHR10 | Ultrasound | 14.53 | dB uV | 38 | Normal
2026-08-16 | LHR10-UPS-01 | UPS System 01 - LHR10 | Ultrasound | 14.17 | dB uV | 38 | Normal
2026-08-17 | LHR10-UPS-01 | UPS System 01 - LHR10 | Ultrasound | 15.41 | dB uV | 38 | Normal
2026-08-18 | LHR10-UPS-01 | UPS System 01 - LHR10 | Ultrasound | 17.18 | dB uV | 38 | Normal
2026-08-19 | LHR10-UPS-01 | UPS System 01 - LHR10 | Ultrasound | 19.19 | dB uV | 38 | Normal
2026-08-20 | LHR10-UPS-01 | UPS System 01 - LHR10 | Ultrasound | 19.41 | dB uV | 38 | Normal
2026-08-21 | LHR10-UPS-01 | UPS System 01 - LHR10 | Ultrasound | 22.44 | dB uV | 38 | Normal
2026-08-22 | LHR10-UPS-01 | UPS System 01 - LHR10 | Ultrasound | 24.29 | dB uV | 38 | Normal
2026-08-23 | LHR10-UPS-01 | UPS System 01 - LHR10 | Ultrasound | 24.89 | dB uV | 38 | Normal
2026-08-24 | LHR10-UPS-01 | UPS System 01 - LHR10 | Ultrasound | 26.91 | dB uV | 38 | Normal

## Detections
Detection_ID | Register_Alert_Ref | Asset_ID | Asset_Name | Failure_Code | Failure_Mode | Severity | Sensors_Corroborating | Confidence_Before_Pct | Confidence_After_Pct | Status
ALT-1003 | ALT-0001 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | V03 | Imbalance | High | 2 of 2 | 74 | 88 | Closed - Resolved
ALT-1004 | ALT-0002 | ORD12-UPS-01 | UPS System 01 - ORD12 | T01 | Loose Electrical Connection | Critical | 2 of 2 | 71 | 89 | Closed - Resolved
ALT-1005 | ALT-0003 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | U02 | Arcing | Critical | 2 of 2 | 76 | 93 | Closed - Resolved
ALT-1006 | ALT-0004 | FRA15-XFMR-01 | Transformer 01 - FRA15 | T04 | Insulation Degradation (suspected) | High | 2 of 2 | 58 | 71 | Under Investigation
ALT-1007 | ALT-0005 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | V02 | Misalignment | Medium | 1 of 3 (vibration only; thermal/ultrasound stayed normal) | 70 | 85 | Closed - Resolved
ALT-1008 | ALT-0006 | SYD12-CHIL-01 | Chiller 01 - SYD12 | V05 | Cavitation | Medium | 1 of 3 (vibration only; no thermal/ultrasound corroboration — driver of the false-positive call) | 62 | 41 | Closed - False Positive
ALT-1009 | ALT-0008 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | U02 | Arcing | Low | 1 of 2 (ultrasound only, below alarm — thermal still normal) | 48 | 61 | Open
ALT-1010 | (new - not yet in register) | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | V04 | Looseness | Medium | 1 of 2 (vibration only; thermal still normal) | 52 | 65 | Recommended
ALT-1011 | (new - not yet in register) | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | T03 | Cooling Failure | High | 1 of 2 (thermal only; vibration still normal) | 55 | 68 | Recommended
ALT-1012 | (new - not yet in register) | LHR10-UPS-01 | UPS System 01 - LHR10 | T02 | Overloaded Circuitry | Critical | 2 of 2 | 69 | 82 | Dispatched

## Recommendations_WorkOrders
Rec_ID | Detection_ID | Asset_ID | Asset_Name | Recommended_Action | Work_Order_ID | WO_Status | Technician_Finding | Outcome | Date_Closed
REC-2003 | ALT-1003 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | Inspect and correct impeller/coupling imbalance within 2 weeks | WO-3003 | Completed | Impeller wear consistent with imbalance signature; rebalanced and corrected. | True positive | 2026-09-18
REC-2004 | ALT-1004 | ORD12-UPS-01 | UPS System 01 - ORD12 | De-energize and re-torque input terminal lug within 48 hours | WO-3004 | Completed | Loose input terminal lug confirmed as heat source; re-torqued and re-tested. | True positive | 2026-09-21
REC-2005 | ALT-1005 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | Isolate and resurface breaker cable lug contact within 24 hours | WO-3005 | Completed | Early-stage arcing confirmed at breaker cable lug; contact resurfaced. | True positive | 2026-09-29
REC-2006 | ALT-1006 | FRA15-XFMR-01 | Transformer 01 - FRA15 | Schedule oil/DGA sampling and IR thermography follow-up within 1 week | WO-1004 | In Progress | Not logged yet — engineering review in progress. | Pending
REC-2007 | ALT-1007 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | Correct coupling misalignment during next exercise run | WO-3006 | Completed | Minor coupling misalignment confirmed and corrected during routine exercise run. | True positive | 2026-10-06
REC-2008 | ALT-1008 | SYD12-CHIL-01 | Chiller 01 - SYD12 | No action — monitor; consider adjusting vibration alarm threshold | — | Not raised | No cavitation or mechanical wear found on inspection; consistent with a momentary flow transient. | False positive | 2026-10-09
REC-2009 | ALT-1009 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Add to next scheduled thermographic scan; re-check ultrasound in 2 weeks | — | Not yet raised | Not logged yet — below alarm threshold, monitoring only. | Pending
REC-2010 | ALT-1010 | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | Inspect fan mounting bolts and belt tension within 2 weeks | — | Not yet raised | Not logged yet — recommendation issued, no work order raised. | Pending
REC-2011 | ALT-1011 | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | Inspect fill media and basin water treatment within 1 week | — | Not yet raised | Not logged yet — recommendation issued, no work order raised. | Pending
REC-2012 | ALT-1012 | LHR10-UPS-01 | UPS System 01 - LHR10 | Redistribute load across output modules and inspect breaker sizing within 48 hours | WO-3010 | Dispatched | Not logged yet — the job is still open. | Pending

## Outcome_Log_Additions
Date_Closed | Asset_ID | Asset_Name | Failure_Code | Predicted | Confidence_Pct | Technician_Found | Classification | Counted_Toward_Accuracy
2026-09-18 | IAD35-PUMP-01 | Pump (Chilled / Condenser Water) 01 - IAD35 | V03 | Imbalance suspected | 88 | Impeller wear consistent with imbalance signature; rebalanced and corrected. | True positive | Yes
2026-09-21 | ORD12-UPS-01 | UPS System 01 - ORD12 | T01 | Loose Electrical Connection suspected | 89 | Loose input terminal lug confirmed as heat source; re-torqued and re-tested. | True positive | Yes
2026-09-29 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | U02 | Arcing suspected | 93 | Early-stage arcing confirmed at breaker cable lug; contact resurfaced. | True positive | Yes
(open) | FRA15-XFMR-01 | Transformer 01 - FRA15 | T04 | Insulation Degradation (suspected) suspected | 71 | Not logged yet — engineering review in progress. | Pending | No - awaiting outcome
2026-10-06 | SIN11-GENS-01 | Standby Generator Set (parent asset) 01 - SIN11 | V02 | Misalignment suspected | 85 | Minor coupling misalignment confirmed and corrected during routine exercise run. | True positive | Yes
2026-10-09 | SYD12-CHIL-01 | Chiller 01 - SYD12 | V05 | Cavitation suspected | 41 | No cavitation or mechanical wear found on inspection; consistent with a momentary flow transient. | False positive | Yes
(open) | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | U02 | Arcing suspected | 61 | Not logged yet — below alarm threshold, monitoring only. | Pending | No - awaiting outcome
(open) | ORD12-AHU-01 | Air Handling Unit (AHU) 01 - ORD12 | V04 | Looseness suspected | 65 | Not logged yet — recommendation issued, no work order raised. | Pending | No - awaiting outcome
(open) | IAD35-CTWR-01 | Cooling Tower 01 - IAD35 | T03 | Cooling Failure suspected | 68 | Not logged yet — recommendation issued, no work order raised. | Pending | No - awaiting outcome
(open) | LHR10-UPS-01 | UPS System 01 - LHR10 | T02 | Overloaded Circuitry suspected | 82 | Not logged yet — the job is still open. | Pending | No - awaiting outcome

## Incident_Downtime_Detail
Incident_ID | Date | Asset_ID_Reference | Asset_Name | Site | Downtime_Hours | Downtime_Note | Customer_Impact | Description | Root_Cause | How_Found
INC-2025-014 | 2025-03-10 | ORD12-UPS-01 | UPS System 01 - ORD12 | Franklin Park Campus - Building 12 | 0 | Redundant leg only; load stayed on active module | No | UPS module fault on redundant leg; load remained on active module. | Capacitor failure (age-related). | BMS Alarm
INC-2025-027 | 2025-06-21 | LHR10-LVSG-01 | LV Switchgear 01 - LHR10 | London Campus - Building 10 | 1.5 | Nuisance trip on non-critical distribution breaker | No | Nuisance trip on non-critical distribution breaker. | Protective relay settings drift. | EPMS Alarm
INC-2025-041 | 2025-08-03 | IAD35-CHIL-01 | Chiller 01 - IAD35 | Ashburn Campus - Building 35 | 0 | N+1 covered; no capacity loss to IT load | No | Reduced chiller capacity during peak cooling demand. | Fouled condenser tubes. | Operator Report + BMS Trend
INC-2025-058 | 2025-10-29 | FRA15-GENS-01 | Standby Generator Set (parent asset) 01 - FRA15 | Hanauer Landstrasse Campus - Building 15 | 0 | Scheduled load-bank test, not a live event | No | Failed to reach rated load during scheduled load-bank test. | Fuel filter restriction. | Scheduled PM (PM-GENS-02)
INC-2026-009 | 2026-02-13 | SIN11-XFMR-01 | Transformer 01 - SIN11 | Loyang Campus - Building 11 | 0 | Corrected same shift | No | Elevated top-oil temperature alarm during high-load period. | Cooling fan controller fault. | BMS Alarm
INC-2026-021 | 2026-05-01 | SYD12-CHIL-01 | Chiller 01 - SYD12 | Erskine Park Campus - Building 12 | 0.5 | N+1 covered; brief transient only | No | Unplanned chiller trip on high discharge pressure. | Condenser water flow restriction. | BMS Alarm
INC-2026-033 | 2026-06-18 | ORD12-PDU-01 | PDU System (Power Distribution Unit) 01 - ORD12 | Franklin Park Campus - Building 12 | 0 | Found on inspection before any load impact | No | Breaker overheating identified during routine inspection. | Loose termination. | Scheduled PM Inspection